## accuracy
2026 OS vs oltc-selector
metric | value
PDFs | 675
Extracted sold_type | 541
Judged (has type + transformer I) | 388
Skipped | 287
exact #1 | 171
#1 family / I / Um (grade or tap differs) | 31
#1 same family, different I or Um | 23
sold type eligible, not #1 (often oil CM vs vacuum CM2, or grade C vs auto B) | 153
oil vs vacuum twin | 1
miss | 9
#1 family+I+Um or better | 52.1% of judged
sold type produced (eligible or better, plus oil/vac twin) | 97.7% of judged

## sales
file | folder | serial | customer | family_folder | sold_type | type_alts | phases | current_a | connection | um_kv | selector_size | tap_code | unit_count | mva | rated_kv | i_a | i_max_a | ust_v | ust_max_v | plus_minus_steps | plus_steps | minus_steps | mdu | text_status | notes
E-M260001 俄罗斯HMR-LIDER.pdf | CM | E-M260001 | 俄罗斯HMR-LIDER | CM | CMIII-600Y/72.5C-14253W |  | III | 600 | Y | 72.5 | C | 14253W | 1 | 105 | 41 |  | 533.5 |  | 1976.7 | 11 |  |  | CMA7 | ok | type_from_oltc_data
E-M260002-003 乌兹别克斯坦CHIRCHIK.pdf | CM | E-M260002-003 | 乌兹别克斯坦CHIRCHIK | CM | [8 empty] | 2 | 25 | [9 empty] | ok | no_type
E-M260004-005 俄罗斯HMR-JSHC.pdf | CM | E-M260004-005 | 俄罗斯HMR-JSHC | CM | [8 empty] | 2 | [10 empty] | ok | page_timeout_at_9; no_type
E-M260006-007 俄罗斯HMR-SIEMENS.pdf | CM | E-M260006-007 | 俄罗斯HMR-SIEMENS | CM | [8 empty] | 2 | [10 empty] | ok | page_timeout_at_9; no_type
E-M260008 俄罗斯HMR-UETM.pdf | CM | E-M260008 | 俄罗斯HMR-UETM | CM | CMIII-500Y/72.5B-10193W |  | III | 500 | Y | 72.5 | B | 10193W | 1 | 40 | 158 | 146.2 | 155.5 | 1368 |  | 8 |  |  | CMA7 | ok | type_from_oltc_data
E-M260009 捷克CEZ.pdf | CM | E-M260009 | 捷克CEZ | CM | CMIII-500Y/126C-10193G |  | III | 500 | Y | 126 | C | 10193G | 1 | [9 empty] | CMA7 | ok | type_from_compact
E-M260010 土耳其HMT-ASTOR.pdf | CM | E-M260010 | 土耳其HMT-ASTOR | CM | CMIII-500Y/72.5C-16150 |  | III | 500 | Y | 72.5 | C | 16150 | 1 | 3 | 31.5 |  |  |  | 3000 |  |  |  | CMA7 | ok | type_from_oltc_data
E-M260011-013 俄罗斯HMR-TOGLIATTI.pdf | CM | E-M260011-013 | 俄罗斯HMR-TOGLIATTI | CM | CMIII-500Y/72.5B-10193W |  | III | 500 | Y | 72.5 | B | 10193W | 3 | 25 | 158 | 91.4 | 97.2 | 1368 |  | 8 |  |  | CMA7 | ok | type_from_oltc_data
E-M260014-015 俄罗斯HMR-TOGLIATTI.pdf | CM | E-M260014-015 | 俄罗斯HMR-TOGLIATTI | CM | CMIII-500Y/72.5B-10193W |  | III | 500 | Y | 72.5 | B | 10193W | 2 | 25 | 158 | 91.4 | 97.2 | 1368 |  | 8 |  |  | CMA7 | ok | type_from_oltc_data
E-M260016 俄罗斯HMR-UETM.pdf | CM | E-M260016 | 俄罗斯HMR-UETM | CM | 3xCMI-1200/170C-14131W |  | I | 1200 |  | 170 | C | 14131W | 3 | 180 | 158 | 657.7 | 747.4 | 1824 |  | 6 |  |  | CMA7 | ok | type_from_oltc_data
E-M260017 俄罗斯HMR-JSHC.pdf | CM | E-M260017 | 俄罗斯HMR-JSHC | CM | [19 empty] | ok | page_timeout_at_9; no_type
E-M260018-019 俄罗斯HMR-JSHC.pdf | CM | E-M260018-019 | 俄罗斯HMR-JSHC | CM | [8 empty] | 2 | [10 empty] | ok | page_timeout_at_9; no_type
E-M260020 俄罗斯HMR-JSHC.pdf | CM | E-M260020 | 俄罗斯HMR-JSHC | CM | [19 empty] | ok | page_timeout_at_10; no_type
E-M260021 俄罗斯HMR-SIEMENS.pdf | CM | E-M260021 | 俄罗斯HMR-SIEMENS | CM | CMIII-500Y/72.5B-10080 |  | III | 500 | Y | 72.5 | B | 10080 | 1 | 18 | 33 | 314.9 | 314.9 |  | 927 |  |  |  | CMA7 | ok | type_from_oltc_data
E-M260022 俄罗斯HMR-SIEMENS.pdf | CM | E-M260022 | 俄罗斯HMR-SIEMENS | CM | [9 empty] | 125 | 230 | [8 empty] | ok | page_timeout_at_11; no_type
E-M260023-024 俄罗斯HMR-SIEMENS.pdf | CM | E-M260023-024 | 俄罗斯HMR-SIEMENS | CM | 3xCMI-800/170C-14131W |  | I | 800 |  | 170 | C | 14131W | 3 | 125 | 121 | 596.4 | 634.5 | 1397 |  | 6 |  |  | CMA7 | ok | type_from_oltc_data
E-M260025 HMPI 售后.pdf | CM | E-M260025 | HMPI 售后 | CM | CMI-1200/72.5C-18351W |  | I | 1200 |  | 72.5 | C | 18351W | 1 | [9 empty] | HMC-3C | ok | po_not_os; type_from_compact
E-M260026 土耳其HMT-ASTOR.pdf | CM | E-M260026 | 土耳其HMT-ASTOR | CM | CMIII-500Y/72.5C-16150 |  | III | 500 | Y | 72.5 | C | 16150 | 1 | 5 | 31.5 | [7 empty] | CMA7 | ok | type_from_oltc_data
E-M260027-028 俄罗斯HMR-SIEMENS.pdf | CM | E-M260027-028 | 俄罗斯HMR-SIEMENS | CM | 3xCMI-800/170C-14131W |  | I | 800 |  | 170 | C | 14131W | 3 | 125 | 121 | 596.4 | 634.5 | 1397 |  | 6 |  |  | CMA7 | ok | type_from_oltc_data
E-M260029 哈萨克斯坦 ASIA TRAFO.pdf | CM | E-M260029 | 哈萨克斯坦 ASIA TRAFO | CM | [8 empty] | 1 | [10 empty] | ok | no_type
E-M260030 俄罗斯HMR-SVEL.pdf | CM | E-M260030 | 俄罗斯HMR-SVEL | CM | 3xCMI-800/170B-14131W |  | I | 800 |  | 170 | B | 14131W | 3 | 125 | 121 | 596 | 678 | 1400 |  | 6 |  |  | CMA7 | ok | type_from_oltc_data
E-M260031 韩国SSANG YONG.pdf | CM | E-M260031 | 韩国SSANG YONG | CM | CMIII-500Y/72.5B-500 | CMIII-500Y/72.5B-1 | III | 500 | Y | 72.5 | B | 500 | 1 | 15 | 46.935 | 185 | 250 | 1123 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-M260032-033 俄罗斯HMR-TOGLIATTI.pdf | CM | E-M260032-033 | 俄罗斯HMR-TOGLIATTI | CM | 3xCMI-1200Y/170C-14131W |  | I | 1200 | Y | 170 | C | 14131W | 3 | 200 | 115 | 1004 | 1068 | 1328 |  | 6 |  |  | CMA7 | ok | type_from_oltc_data
E-M260034 俄罗斯HMR-UETM.pdf | CM | E-M260034 | 俄罗斯HMR-UETM | CM | CMIII-500Y/126B-10193W |  | III | 500 | Y | 126 | B | 10193W | 6 | 63 | 158 | 230.2 | 244.9 | 1368 |  | 8 |  |  | CMA7 | ok | type_from_oltc_data
E-M260035 俄罗斯HMR-SIEMENS.pdf | CM | E-M260035 | 俄罗斯HMR-SIEMENS | CM | CMIII-500Y/72.5B-10193W |  | III | 500 | Y | 72.5 | B | 10193W | 1 | 32 | 158 | 117 | 125 | 1368 |  | 8 |  |  | CMA7 | ok | type_from_oltc_data
E-M260036 俄罗斯HMR-SIEMENS.pdf | CM | E-M260036 | 俄罗斯HMR-SIEMENS | CM | CMIII-500Y/72.5B-10191W |  | III | 500 | Y | 72.5 | B | 10191W | 1 | 80 | 115 | 401.6 | 424.3 | 1181 |  | 9 |  |  | CMA7 | ok | type_from_oltc_data
E-M260037 俄罗斯HMR-SIEMENS.pdf | CM | E-M260037 | 俄罗斯HMR-SIEMENS | CM | CMIII-500Y/72.5B-14273W |  | III | 500 | Y | 72.5 | B | 14273W | 1 | 40 | 230 | 100.4 | 105.7 | 1328 |  | 12 |  |  | CMA7 | ok | type_from_oltc_data
E-M260038 俄罗斯HMR-TOGLIATTI.pdf | CM | E-M260038 | 俄罗斯HMR-TOGLIATTI | CM | CMIII-500Y/72.5B-14273W |  | III | 500 | Y | 72.5 | B | 14273W | 1 | 40 | 230 | 100.41 | 104.59 | 1328 |  | 12 |  |  | CMA7 | ok | type_from_oltc_data
E-M260039 俄罗斯HMR-SIEMENS.pdf | CM | E-M260039 | 俄罗斯HMR-SIEMENS | CM | 3xCMI-800/170C-14131W |  | I | 800 |  | 170 | C | 14131W | 3 | 125 | 121 | 596.4 | 634.5 | 1397 |  | 6 |  |  | CMA7 | ok | type_from_oltc_data
E-M260040-041 俄罗斯HMR-JSHC.pdf | CM | E-M260040-041 | 俄罗斯HMR-JSHC | CM | CMIII-500Y/72.5B-10193W |  | III | 500 | Y | 72.5 | B | 10193W | 2 | 25 | 158 | 91.4 | 97.2 | 1368.3 |  | 8 |  |  | CMA7 | ok | type_from_oltc_data
E-M260042 乌兹别克斯坦CHIRCHIQ.pdf | CM | E-M260042 | 乌兹别克斯坦CHIRCHIQ | CM | [9 empty] | 25 | 158 |  |  | 1368 | [5 empty] | ok | no_type
E-M260044 俄罗斯HMR-JSHC.pdf | CM | E-M260044 | 俄罗斯HMR-JSHC | CM | CMIII-500Y/72.5B-14273W |  | III | 500 | Y | 72.5 | B | 14273W | 1 | 125 | 230 | 313.8 | 330.3 | 1328 |  | 12 |  |  | CMA7 | ok | type_from_oltc_data
E-M260045 俄罗斯HMR-JSHC.pdf | CM | E-M260045 | 俄罗斯HMR-JSHC | CM | [9 empty] | 250 | 230 | 628 | 668 | 2656 |  | 6 |  |  | CMA7 | ok | no_type
E-M260046乌兹别克斯坦CHIRCHIQ.pdf | CM | E-M260046 | 乌兹别克斯坦CHIRCHIQ | CM | [9 empty] | 16 | [9 empty] | ok | no_type
E-M260047乌兹别克斯坦CHIRCHIQ.pdf | CM | E-M260047 | 乌兹别克斯坦CHIRCHIQ | CM | [10 empty] | 158 | [8 empty] | ok | no_type
E-M260048-049 俄罗斯HMR-SIEMENS.pdf | CM | E-M260048-049 | 俄罗斯HMR-SIEMENS | CM | CMIII-500Y/72.5B-14273W |  | III | 500 | Y | 72.5 | B | 14273W | 2 | 40 | 230 | 101 | 106 | 1328 |  | 12 |  |  | CMA7 | ok | type_from_oltc_data
E-M260050-052 土耳其HMT-Europower.pdf | CM | E-M260050-052 | 土耳其HMT-Europower | CM | CMIII-500Y/72.5C-16150 |  | III | 500 | Y | 72.5 | C | 16150 | 3 | 3 | 31.5 |  |  |  | 1298 |  |  |  |  | ok | type_from_oltc_data
E-M260053-072 土耳其HMT-Europower.pdf | CM | E-M260053-072 | 土耳其HMT-Europower | CM | CMIII-500Y/72.5C-16150 |  | III | 500 | Y | 72.5 | C | 16150 | 20 | 5 | 31.5 |  |  |  | 1422 |  |  |  | CMA7 | ok | type_from_oltc_data
E-M260073-075 土耳其HMT-Europower.pdf | CM | E-M260073-075 | 土耳其HMT-Europower | CM | CMIII-500Y/72.5C-16150 |  | III | 500 | Y | 72.5 | C | 16150 | 3 | 5 | 31.5 |  |  |  | 1422 |  |  |  | CMA7 | ok | type_from_oltc_data
E-M260076-081 土耳其HMT-Europower.pdf | CM | E-M260076-081 | 土耳其HMT-Europower | CM | CMIII-500Y/72.5C-16150 |  | III | 500 | Y | 72.5 | C | 16150 | 6 | 5 | 34.5 |  |  |  | 1576 |  |  |  | CMA7 | ok | type_from_oltc_data
E-M260082-086 土耳其HMT-Europower.pdf | CM | E-M260082-086 | 土耳其HMT-Europower | CM | CMIII-500Y/72.5C-16150 |  | III | 500 | Y | 72.5 | C | 16150 | 5 | 5 | 34.5 |  |  |  | 1576 |  |  |  | CMA7 | ok | type_from_oltc_data
E-M260087-088 哈萨克斯坦 ASIA TRAFO.pdf | CM | E-M260087-088 | 哈萨克斯坦 ASIA TRAFO | CM | [8 empty] | 1 | [10 empty] | ok | no_type
E-M260089-090 俄罗斯HMR-SIEMENS.pdf | CM | E-M260089-090 | 俄罗斯HMR-SIEMENS | CM | [8 empty] | 2 | [10 empty] | ok | page_timeout_at_9; no_type
E-M260091 土耳其HMT-ASTOR.pdf | CM | E-M260091 | 土耳其HMT-ASTOR | CM | CMIII-500Y/72.5C-16150 |  | III | 500 | Y | 72.5 | C | 16150 | 1 | 3 | 31.5 | [7 empty] | CMA7 | ok | type_from_oltc_data
E-M260092,E-M260094 俄罗斯HMR-LIDER.pdf | CM | E-M260092,E-M260094 | 俄罗斯HMR-LIDER | CM | CMI-500/170C-10193W |  | I | 500 |  | 170 | C | 10193W | 2 | 63 | 121 | 301 | 316 | 1048 |  | 8 |  |  | CMA7 | ok | type_from_oltc_data
E-M260093 土耳其HMT-Eren Transformer.pdf | CM | E-M260093 | 土耳其HMT-Eren Transformer | CM | CMIII-600Y/72.5C-14271G |  | III | 600 | Y | 72.5 | C | 14271G | 1 | 2.5 | 21 | 68.7 | [6 empty] | SHM-D | ok | type_from_oltc_data
E-M260095-096 俄罗斯HMR-PMTT.pdf | CM | E-M260095-096 | 俄罗斯HMR-PMTT | CM | 3xCMI-1200/170B-14131W |  | I | 1200 |  | 170 | B | 14131W | 3 | 250 | 158 | 913.5 | 971.8 | 1852.9 |  | 6 |  |  | CMA7 | ok | type_from_oltc_data
E-M260097-098 俄罗斯HMR-JSHC.pdf | CM | E-M260097-098 | 俄罗斯HMR-JSHC | CM | [8 empty] | 2 | [10 empty] | ok | page_timeout_at_7; no_type
E-M260099-101 俄罗斯HMR-UETM.pdf | CM | E-M260099-101 | 俄罗斯HMR-UETM | CM | CMIII-500Y/126B-10193W |  | III | 500 | Y | 126 | B | 10193W | 3 | 63 | 158 | 230.2 | 244.9 | 1368 |  | 8 |  |  | CMA7 | ok | type_from_oltc_data
E-M260102 委内瑞拉 VALECILLOS.pdf | CM | E-M260102 | 委内瑞拉 VALECILLOS | CM | CMIII-500Y/126B-10091W | CMIII-500Y/126B-10100 | III | 500 | Y | 126 | B | 10091W | 1 | 20 | 115 | 100.41 |  | 1660 |  |  |  |  | CMA7 | ok | type_from_compact
E-M260103 俄罗斯HMR-PMTT.pdf | CM | E-M260103 | 俄罗斯HMR-PMTT | CM | 3xCMI-1200/170B-14131W |  | I | 1200 |  | 170 | B | 14131W | 3 | [9 empty] | CMA7 | ok | type_from_compact
E-M260104-105 哈萨克斯坦ASIATRAFO .pdf | CM | E-M260104-105 | 哈萨克斯坦ASIATRAFO | CM | CMI-800/126-14131W |  | I | 800 |  | 126 |  | 14131W | 2 | 125 | 121 |  |  | 1397 |  | 6 |  |  |  | ok | type_from_oltc_data
E-M260106-107 俄罗斯HMR-SIEMENS.pdf | CM | E-M260106-107 | 俄罗斯HMR-SIEMENS | CM | [19 empty] | scanned_or_empty | page_timeout_at_8
E-M260108 俄罗斯HMR-SIEMENS.pdf | CM | E-M260108 | 俄罗斯HMR-SIEMENS | CM | 3xCMI-1200/170C-14131W |  | I | 1200 |  | 170 | C | 14131W | 3 | 200 | 115 |  |  | 1328 |  | 6 |  |  | CMA7 | ok | type_from_oltc_data
E-M260109 俄罗斯HMR-SVEL.pdf | CM | E-M260109 | 俄罗斯HMR-SVEL | CM | 3xCMI-1200/170B-14131W |  | I | 1200 |  | 170 | B | 14131W | 3 | 200 | 121 | 954 | 1084 | 1346 |  | 6 |  |  | CMA7 | ok | type_from_oltc_data
E-M260110 俄罗斯HMR-UETM.pdf | CM | E-M260110 | 俄罗斯HMR-UETM | CM | CMIII-500Y/126B-10193W |  | III | 500 | Y | 126 | B | 10193W | 1 | [9 empty] | HMC-3C | ok | type_from_compact
E-M260111 俄罗斯HMR-SIEMENS.pdf | CM | E-M260111 | 俄罗斯HMR-SIEMENS | CM | 3xCMI-1500/126B-14131W | CMI-1500/126B-14131W | I | 1500 |  | 126 | B | 14131W | 3 | 250 | 121 | 1192.9 | 1296.6 | 1398 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-M260112 土耳其HMT-ZTR.pdf | CM | E-M260112 | 土耳其HMT-ZTR | CM | CMIII-500Y/72.5B-10191W |  | III | 500 | Y | 72.5 | B | 10191W | 1 | 80 | [9 empty] | ok | po_not_os; type_from_compact
E-M260113 俄罗斯HMR-JSHC.pdf | CM | E-M260113 | 俄罗斯HMR-JSHC | CM | 3xCMI-1500/170C-14131W |  | I | 1500 |  | 170 | C | 14131W | 3 | 250 | 230 | 1193 | 1269 |  |  | 6 |  |  | CMA7 | ok | type_from_oltc_data
E-M260114 俄罗斯HMR-PMTT.pdf | CM | E-M260114 | 俄罗斯HMR-PMTT | CM | 3xCMI-800/252B-14131W |  | I | 800 |  | 252 | B | 14131W | 3 | 250 | 330 | 627.6 | 667.6 | 2688.9 |  | 6 |  |  | CMA7 | ok | type_from_oltc_data
E-M260115 土耳其-Taskin Consultancy.pdf | CM | E-M260115 | 土耳其-Taskin Consultancy | CM | CMIII-600Y/72.5C-18531G | SVIII-500D/40.5-10191W | III | 600 | Y | 72.5 | C | 18531G | 1 | 15 | [8 empty] | SHM-D | ok | po_not_os; type_from_compact
E-M260116-117 俄罗斯HMR-PMTT.pdf | CM | E-M260116-117 | 俄罗斯HMR-PMTT | CM | 3xCMI-1200/170B-14131W |  | I | 1200 |  | 170 | B | 14131W | 3 | 200 | 330 | 1004.1 | 1068.2 | 1413.5 |  | 6 |  |  | CMA7 | ok | type_from_oltc_data
E-M260118-119 俄罗斯HMR-SVEL.pdf | CM | E-M260118-119 | 俄罗斯HMR-SVEL | CM | CMIII-500Y/72.5C-14273W |  | III | 500 | Y | 72.5 | C | 14273W | 2 | 40 | 230 | 100 | 106 | 1330 |  | 12 |  |  | CMA7 | ok | type_from_oltc_data
E-M260120-121 土耳其-Sönmez Trafo.pdf | CM | E-M260120-121 | 土耳其-Sönmez Trafo | CM | CMIII-500Y/72.5C-18170 |  | III | 500 | Y | 72.5 | C | 18170 | 2 | 5 | 20.5 |  | 141 |  | 1398 |  |  |  | CMA7 | ok | type_from_oltc_data
E-M260122 俄罗斯HMR-JSHC.pdf | CM | E-M260122 | 俄罗斯HMR-JSHC | CM | 3xCMI-1500Y/126B-14131W |  | I | 1500 | Y | 126 | B | 14131W | 3 | 250 | 220 | 1193 | 1269 | 1397 |  | 6 |  |  | CMA7 | ok | type_from_oltc_data
E-M260123 俄罗斯HMR-PMTT.pdf | CM | E-M260123 | 俄罗斯HMR-PMTT | CM | 3xCMI-1200/170B-14131W |  | I | 1200 |  | 170 | B | 14131W | 3 | 200 | 330 | 1004.1 | 1068.2 | 1413.5 |  | 6 |  |  | CMA7 | ok | type_from_oltc_data
E-M260124-126 阿塞拜疆 ATEF.pdf | CM | E-M260124-126 | 阿塞拜疆 ATEF | CM | 3xCMI-1500/170C-14131W |  | I | 1500 |  | 170 | C | 14131W | 3 | 250 | 121 | 1193 | 1356 | 1398 |  | 6 |  |  | CMA7 | ok | type_from_compact
E-M260127-135 土耳其HMT-ASTOR.pdf | CM | E-M260127-135 | 土耳其HMT-ASTOR | CM | CMIII-500Y/72.5C-16150 |  | III | 500 | Y | 72.5 | C | 16150 | 9 | 5 | 31.5 | [7 empty] | CMA7 | ok | type_from_oltc_data
E-M260136-138 土耳其HMT-ASTOR.pdf | CM | E-M260136-138 | 土耳其HMT-ASTOR | CM | CMIII-500Y/72.5C-16150 |  | III | 500 | Y | 72.5 | C | 16150 | 3 | 5 | 31.5 | [7 empty] | CMA7 | ok | type_from_oltc_data
E-M260139 土耳其HMT-ASTOR.pdf | CM | E-M260139 | 土耳其HMT-ASTOR | CM | CMIII-500Y/72.5C-16150 |  | III | 500 | Y | 72.5 | C | 16150 | 1 | 2 | 31.5 | [7 empty] | CMA7 | ok | type_from_oltc_data
E-M260140 俄罗斯HMR-SVEL.pdf | CM | E-M260140 | 俄罗斯HMR-SVEL | CM | CMIII-500Y/72.5C-14273W |  | III | 500 | Y | 72.5 | C | 14273W | 1 | 100 | 230 | 251 | 264 | 1328 |  | 12 |  |  | CMA7 | ok | type_from_oltc_data
E-M260141-142 俄罗斯HMR-JSHC.pdf | CM | E-M260141-142 | 俄罗斯HMR-JSHC | CM | 3xCMI-1500Y/170C-14131W |  | I | 1500 | Y | 170 | C | 14131W | 3 | 250 | 220 |  |  |  |  | 6 |  |  | CMA7 | ok | type_from_oltc_data
E-M260143 印尼GE UNINDO.pdf | CM | E-M260143 | 印尼GE UNINDO | CM | CMIII-500Y/126DE-14273W | CMIII-500Y/126DE-14273G ¦ CVIII-500Y/126-14273W ¦ CVIII-350Y/72.5-12233W ¦ CVIII-350Y/72.51-2233W | III | 500 | Y | 126 | DE | 14273W | 1 | 75 | 220 | 197 | 231.6 | 1588 |  | 24 |  |  | CMA7 | ok | type_from_oltc_data
E-M260144 俄罗斯HMR-SIEMENS.pdf | CM | E-M260144 | 俄罗斯HMR-SIEMENS | CM | CMIII-500Y/72.5C-10193W |  | III | 500 | Y | 72.5 | C | 10193W | 1 | 125 | 330 | 218.7 | 232.7 | 2858 |  | 8 |  |  | CMA7 | ok | type_from_oltc_data
E-M260145-147 俄罗斯HMR-SIEMENS.pdf | CM | E-M260145-147 | 俄罗斯HMR-SIEMENS | CM | 3xCMI-800/170B-14131W |  | I | 800 |  | 170 | B | 14131W | 3 | 125 | 330 | 628 | 668 | 1328 |  | 6 |  |  | CMA7 | ok | type_from_oltc_data
E-M260148-150 土耳其HMT-ASTOR.pdf | CM | E-M260148-150 | 土耳其HMT-ASTOR | CM | CMIII-500Y/72.5C-16150 |  | III | 500 | Y | 72.5 | C | 16150 | 3 | 5 | 31.5 | [7 empty] | CMA7 | ok | type_from_oltc_data
E-M260151 哈萨克斯坦ASIATRAFO .pdf | CM | E-M260151 | 哈萨克斯坦ASIATRAFO | CM | CMIII-500Y/72.5-10193W |  | III | 500 | Y | 72.5 |  | 10193W | 2 | 63 |  |  | 368 | 794 |  | 8 |  |  |  | ok | type_from_oltc_data
E-M260152-161 出口土耳其HMT-Europower.pdf | CM | E-M260152-161 | 出口土耳其HMT-Europower | CM | CMIII-500Y/72.5C-16150 |  | III | 500 | Y | 72.5 | C | 16150 | 10 | 5 | 34.5 |  |  |  | 1576 |  |  |  | CMA7 | ok | type_from_oltc_data
E-M260162 印尼HMPI 售后.pdf | CM | E-M260162 | 印尼HMPI 售后 | CM | CMI-1200/72.5C-18351W |  | I | 1200 |  | 72.5 | C | 18351W | 1 | [10 empty] | ok | po_not_os; type_from_compact
E-M260163 俄罗斯HMR-PMTT.pdf | CM | E-M260163 | 俄罗斯HMR-PMTT | CM | 3xCMI-1200/170B-14131W |  | I | 1200 |  | 170 | B | 14131W | 3 | 200 | 330 | 1004.1 | 1068.2 | 1413.5 |  | 6 |  |  | CMA7 | ok | type_from_oltc_data
E-M260164 土耳其HMT-ASTOR.pdf | CM | E-M260164 | 土耳其HMT-ASTOR | CM | CMIII-500Y/72.5C-16150 |  | III | 500 | Y | 72.5 | C | 16150 | 1 | 3 | 31.5 | [7 empty] | CMA7 | ok | type_from_oltc_data
E-M260165 俄罗斯HMR-SIEMENS.pdf | CM | E-M260165 | 俄罗斯HMR-SIEMENS | CM | [9 empty] | 200 | 330 | 1004 | 1068.2 | 1328 |  | 6 |  |  | CMA7 | ok | no_type
E-M260166 俄罗斯HMR-SIEMENS.pdf | CM | E-M260166 | 俄罗斯HMR-SIEMENS | CM | [9 empty] | 200 | 330 | 1004 | 1068.2 | 1328 |  | 6 |  |  | CMA7 | ok | no_type
E-M260167-168 土耳其HMT-ATS Trafo.pdf | CM | E-M260167-168 | 土耳其HMT-ATS Trafo | CM | CMIII-600Y/72.5B-10173G |  | III | 600 | Y | 72.5 | B | 10173G | 2 | 30 | 33 | 524.9 | 575.2 | 238.2 |  | 7 |  |  | CMA7 | ok | type_from_oltc_data
E-CMD260001 俄罗斯HMR-PMTT.pdf | CMD | E-CMD260001 | 俄罗斯HMR-PMTT | CMD | CMDIII-1000Y/72.5C-10193W |  | III | 1000 | Y | 72.5 | C | 10193W | 1 | 250 | 121 | 904.2 | 983 |  | 1417 | 8 |  |  | CMA7 | ok | type_from_oltc_data
E-CMD260004-005 俄罗斯HMR-TOGLIATTI.pdf | CMD | E-CMD260004-005 | 俄罗斯HMR-TOGLIATTI | CMD | CMDI-1600/252C-14130 |  | I | 1600 |  | 252 | C | 14130 | 2 | 167 |  | 1258 | 1322 | 2656 |  | 6 |  |  | CMA7 | ok | type_from_oltc_data
E-CMD260006 俄罗斯HMR-UETM.pdf | CMD | E-CMD260006 | 俄罗斯HMR-UETM | CMD | CMDIII-1000Y/72.5B-10193W |  | III | 1000 | Y | 72.5 | B | 10193W | 1 | 40 | 36.75 | 628.4 | 668.4 | 377 |  | 8 |  |  | CMA7 | ok | type_from_oltc_data
E-CMD260007 俄罗斯HMR-Remenergo.pdf | CMD | E-CMD260007 | 俄罗斯HMR-Remenergo | CMD | CMDIII-1000Y/72.5B-10193W |  | III | 1000 | Y | 72.5 | B | 10193W | 1 | 16 | 10.5 | 880 | 924 | 91 |  | 8 |  |  | CMA7 | ok | type_from_oltc_data
E-CMD260008 俄罗斯HMR-PMTT.pdf | CMD | E-CMD260008 | 俄罗斯HMR-PMTT | CMD | CMDI-1600/252C-14130 |  | I | 1600 |  | 252 | C | 14130 | 1 | 167 | 11 | 1257.6 | 1321.4 | 2683 |  | 6 |  |  | CMA7 | ok | type_from_oltc_data
E-CMD260009-010 俄罗斯HMR-PMTT.pdf | CMD | E-CMD260009-010 | 俄罗斯HMR-PMTT | CMD | CMDI-1600/252C-14130 |  | I | 1600 |  | 252 | C | 14130 | 1 | 167 | 10.5 | 1257.6 | 1321.4 |  |  | 6 |  |  | CMA7 | ok | type_from_oltc_data
E-CMD260011-013 俄罗斯HMR-PMTT.pdf | CMD | E-CMD260011-013 | 俄罗斯HMR-PMTT | CMD | CMDI-1600/252C-14130 |  | I | 1600 |  | 252 | C | 14130 | 1 | 167 | 38.5 | 1257.6 | 1321.4 |  |  | 6 |  |  | CMA7 | ok | type_from_oltc_data
E-CMD260014-015 俄罗斯HMR-PMTT.pdf | CMD | E-CMD260014-015 | 俄罗斯HMR-PMTT | CMD | [8 empty] | 2 | [10 empty] | ok | page_timeout_at_8; no_type
E-V260001-002 哈萨克斯坦KENTAU.pdf | CV | E-V260001-002 | 哈萨克斯坦KENTAU | CV | [8 empty] | 2 | [10 empty] | ok | no_type
E-V260003 泰国 Tirathai.pdf | CV | E-V260003 | 泰国 Tirathai | CV | CVIII-350D/40.5-12233G |  | III | 350 | D | 40.5 |  | 12233G | 1 | 2 | 6.93 | 133.3 | 266.62 | 346.5 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-V260004-005 越南 HLG-MBT.pdf | CV | E-V260004-005 | 越南 HLG-MBT | CV | CVIII-350D/40.5-10193W |  | III | 350 | D | 40.5 |  | 10193W | 2 | 12.5 | 35 | 207 | 227 | 257 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-V260006-010 乌兹别克斯坦CHIRCHIK.pdf | CV | E-V260006-010 | 乌兹别克斯坦CHIRCHIK | CV | [8 empty] | 5 | 18 | 35 | 330 | 350 | [5 empty] | CMA7 | ok | po_not_os; no_type
E-V260011 哈萨克斯坦ASIATRAFO.pdf | CV | E-V260011 | 哈萨克斯坦ASIATRAFO | CV | [8 empty] | 1 | [9 empty] | SHM-D | ok | no_type
E-V260012 南非-ATM.pdf | CV | E-V260012 | 南非-ATM | CV | SVIII-500Y/40.5-10193W |  | III | 500 | Y | 40.5 |  | 10193W | 2 | 12.5 | 24 | 328 | 386 | 275 |  | 17 |  |  | CMA7 | ok | type_from_compact
E-V260013-014 哈萨克斯坦KENTAU.pdf | CV | E-V260013-014 | 哈萨克斯坦KENTAU | CV | [8 empty] | 2 | [10 empty] | ok | no_type
E-V260015 印尼BAMBANG.pdf | CV | E-V260015 | 印尼BAMBANG | CV | CVIII-350D/40.5-10193W |  | III | 350 | D | 40.5 |  | 10193W | 1 | 2.5 | 20 | 72.17 | 103 | 144.3 |  |  | 4 | 12 | CMA7 | ok | type_from_compact
E-V260016-017 哈萨克斯坦KENTAU.pdf | CV | E-V260016-017 | 哈萨克斯坦KENTAU | CV | [8 empty] | 2 | [10 empty] | ok | no_type
E-V260018-019 哈萨克斯坦KENTAU.pdf | CV | E-V260018-019 | 哈萨克斯坦KENTAU | CV | CVIII-350Y/72.5-10191W | SYXZZ-40.5-200-9 | III | 350 | Y | 72.5 |  | 10191W | 2 | 46 | [8 empty] | SHM-D | ok | type_from_compact
E-V260020-021 印度TOSHIBA.pdf | CV | E-V260020-021 | 印度TOSHIBA | CV | CVIII-350D/40.5-10193G |  | III | 350 | D | 40.5 |  | 10193G | 2 | 10 | [8 empty] | SHM-D | ok | po_not_os; type_from_compact
E-V260022 俄罗斯HMR-LIDER.pdf | CV | E-V260022 | 俄罗斯HMR-LIDER | CV | CVIII-350D/40.5-10131G |  | III | 350 | D | 40.5 |  | 10131G | 1 | 2.5 | 35 | 41.2 | 43.9 | 306 |  |  | 6 | 5 | CMA7 | ok | type_from_oltc_data
E-V260023-024 俄罗斯HMR-TOGLIATTI.pdf | CV | E-V260023-024 | 俄罗斯HMR-TOGLIATTI | CV | CVIII-350Y/72.5-10191W |  | III | 350 | Y | 72.5 |  | 10191W | 2 | 40 | 115 | 200.8 | 212.1 | 1182 |  | 9 |  |  | CMA7 | ok | type_from_oltc_data
E-V260025-026 土耳其HMT-Nexans Maroc.pdf | CV | E-V260025-026 | 土耳其HMT-Nexans Maroc | CV | CVIII-350/12-233 | CVIII-350D/40.5-12233W | III | 350 |  | 12 |  | 233 | 2 | 10 | [5 empty] | 10 |  |  | CMA7 | ok | type_from_oltc_data
E-V260027-028 俄罗斯HMR-UETM.pdf | CV | E-V260027-028 | 俄罗斯HMR-UETM | CV | SVIII-500Y/72.5-10193W |  | III | 500 | Y | 72.5 |  | 10193W | 6 | 25 | 36.75 | 393 | 418 | 318 |  | 8 |  |  | CMA7 | ok | type_from_oltc_data
E-V260029 加拿大HMUS-NORTHERN.pdf | CV | E-V260029 | 加拿大HMUS-NORTHERN | CV | CVIII-350D/40.5-10193W |  | III | 350 | D | 40.5 |  | 10193W | 3 | 9.375 | 27.6 | 114 |  | 345 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-V260030 加拿大HMUS-NORTHERN.pdf | CV | E-V260030 | 加拿大HMUS-NORTHERN | CV | CVIII-350D/40.5-10193W |  | III | 350 | D | 40.5 |  | 10193W | 3 | 9.375 | 27.6 | 196.1 |  | 216.65 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-V260031-033 土耳其HMT-Europower Enerji.pdf | CV | E-V260031-033 | 土耳其HMT-Europower Enerji | CV | CVIII-350D/40.5-14131W |  | III | 350 | D | 40.5 |  | 14131W | 3 | 20 | 34.5 | 193.2 | 222.2 | 498.5 |  |  | 3 | 9 | CMA7 | ok | type_from_oltc_data
E-V260034-035 哈萨克斯坦KENTAU.pdf | CV | E-V260034-035 | 哈萨克斯坦KENTAU | CV | [8 empty] | 2 | [10 empty] | ok | no_type
E-V260036-038 华明印尼 PT Symphos.pdf | CV | E-V260036-038 | 华明印尼 PT Symphos | CV | SVIII-500D/40.5-10193W | SVIII-500D/40.5-1 | III | 500 | D | 40.5 |  | 10193W | 3 | 10 | 20 | 288.68 | 412.39 | 216.51 |  |  | 0 | 16 | SHM-D, SHM-K | ok | type_from_oltc_data
E-V260039 浙江工自仪网络有限公司 售后 - 副本.pdf | CV | E-V260039 | 浙江工自仪网络有限公司 售后 - 副本 | CV | [19 empty] | ok | no_type
E-V260040-041 华明印尼 PT Symphos.pdf | CV | E-V260040-041 | 华明印尼 PT Symphos | CV | CVIII-350D/40.5-10193W | CVIII-350D/40.5-1 | III | 350 | D | 40.5 |  | 10193W | 2 | 5 | 20 | 144.34 | 206.2 | 216.51 |  |  | 0 | 16 | SHM-D, SHM-K | ok | type_from_oltc_data
E-V260042 俄罗斯HMR-SVEL.pdf | CV | E-V260042 | 俄罗斯HMR-SVEL | CV | CVIII-350D/40.5-10191W |  | III | 350 | D | 40.5 |  | 10191W | 1 | 2.5 | 11 | 75.6 | 80.6 | 165 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-V260043-044 俄罗斯HMR-TOGLIATTI.pdf | CV | E-V260043-044 | 俄罗斯HMR-TOGLIATTI | CV | SVIII-500Y/40.5-10193W |  | III | 500 | Y | 40.5 |  | 10193W | 2 | 25 | 36.75 | 392.8 | 417.8 | 551 |  | 8 |  |  | CMA7 | ok | type_from_oltc_data
E-V260045-047 土耳其HMT-MEKSAN.pdf | CV | E-V260045-047 | 土耳其HMT-MEKSAN | CV | CVIII-350D/40.5-10090 |  | III | 350 | D | 40.5 |  | 10090 | 3 | 15 | 33 | 151.5 | 178.3 | 825 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-V260048 巴西COMTRAFO.pdf | CV | E-V260048 | 巴西COMTRAFO | CV | CVIII-350D/72.5-10193W |  | III | 350 | D | 72.5 |  | 10193W | 1 | 15 | 69 | 72.5 | 80.5 | 862.5 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-V260049 土耳其HMT-ZTR.pdf | CV | E-V260049 | 土耳其HMT-ZTR | CV | CVIII-350Y/72.5-10191W |  | III | 350 | Y | 72.5 |  | 10191W | 1 | 10 | [8 empty] | HMC-3C | ok | po_not_os; type_from_compact
E-V260050 印度尼西亚 PT Symphos.pdf | CV | E-V260050 | 印度尼西亚 PT Symphos | CV | CVIII-350D/40.5-12233W |  | III | 350 | D | 40.5 |  | 12233W | 1 | 10 | 20 | 166.67 | 222.22 | 500 |  | 10 |  |  | SHM-D, SHM-K | ok | type_from_oltc_data
E-V260051-052 俄罗斯HMR-JSHC.pdf | CV | E-V260051-052 | 俄罗斯HMR-JSHC | CV | [8 empty] | 2 | [10 empty] | ok | page_timeout_at_8; no_type
E-V260053 土耳其HMT-ZTR.pdf | CV | E-V260053 | 土耳其HMT-ZTR | CV | CVIII-350Y/72.5-10191W |  | III | 350 | Y | 72.5 |  | 10191W | 1 | 40 | [8 empty] | HMC-3C | ok | po_not_os; type_from_compact
E-V260054-063 乌兹别克斯坦CHIRCHIK.pdf | CV | E-V260054-063 | 乌兹别克斯坦CHIRCHIK | CV | [8 empty] | 10 | 18 | 35 | 330 | 350 | [5 empty] | CMA7 | ok | po_not_os; no_type
E-V260064-065 哈萨克斯坦KENTAU.pdf | CV | E-V260064-065 | 哈萨克斯坦KENTAU | CV | [8 empty] | 2 | [10 empty] | ok | no_type
E-V260066-067 哈萨克斯坦KENTAU.pdf | CV | E-V260066-067 | 哈萨克斯坦KENTAU | CV | [8 empty] | 2 | [10 empty] | ok | no_type
E-V260068-069 哈萨克斯坦KENTAU.pdf | CV | E-V260068-069 | 哈萨克斯坦KENTAU | CV | [8 empty] | 2 | [10 empty] | ok | no_type
E-V260070 华明印尼 ALLIS - 副本.pdf | CV | E-V260070 | 华明印尼 ALLIS - 副本 | CV | [18 empty] | CMA7 | ok | po_not_os; no_type
E-V260070 华明印尼 ALLIS.pdf | CV | E-V260070 | 华明印尼 ALLIS | CV | [18 empty] | CMA7 | ok | po_not_os; no_type
E-V260071 巴西Blutrafo.pdf | CV | E-V260071 | 巴西Blutrafo | CV | CVIII-350D/72.5-10193W |  | III | 350 | D | 72.5 |  | 10193W | 1 | 6.25 | 69 | 52.3 |  | 862 |  |  |  |  | SHM-D, SHM-K | ok | type_from_oltc_data
E-V260072 哈萨克斯坦ASIATRAFO .pdf | CV | E-V260072 | 哈萨克斯坦ASIATRAFO | CV | [19 empty] | scanned_or_empty
E-V260073 俄罗斯HMR-SVEL.pdf | CV | E-V260073 | 俄罗斯HMR-SVEL | CV | CVIII-350Y/72.5-10191W |  | III | 350 | Y | 72.5 |  | 10191W | 1 | 40 | 115 | 201 | 212 | 1182 |  | 9 |  |  | CMA7 | ok | type_from_oltc_data
E-V260074-075 孟加拉国System Engineering.pdf | CV | E-V260074-075 | 孟加拉国System Engineering | CV | CVIII-350D/40.5-10193G |  | III | 350 | D | 40.5 |  | 10193G | 1 | 2.5 |  | 43.74 | 50.3 | 412.5 |  |  |  |  | SHM-D | ok | type_from_oltc_data
E-V260076 乌兹别克斯坦CHIRCHIQ.pdf | CV | E-V260076 | 乌兹别克斯坦CHIRCHIQ | CV | [9 empty] | 10 | 36.75 | [7 empty] | SHM-D | ok | no_type
E-V260077 乌兹别克斯坦CHIRCHIQ.pdf | CV | E-V260077 | 乌兹别克斯坦CHIRCHIQ | CV | [19 empty] | ok | no_type
E-V260078 土耳其HMT-Nexans Maroc.pdf | CV | E-V260078 | 土耳其HMT-Nexans Maroc | CV | CVIII-350/12-233 | CVIII-350Y/72.5-12233W | III | 350 |  | 12 |  | 233 | 1 | 7 | [5 empty] | 10 |  |  | CMA7 | ok | type_from_oltc_data
E-V260079-080 哈萨克斯坦ASIATRAFO .pdf | CV | E-V260079-080 | 哈萨克斯坦ASIATRAFO | CV | [8 empty] | 2 | [10 empty] | ok | no_type
E-V260081-082 哈萨克斯坦ASIATRAFO .pdf | CV | E-V260081-082 | 哈萨克斯坦ASIATRAFO | CV | [8 empty] | 2 | [10 empty] | ok | no_type
E-V260083 哈萨克斯坦ASIATRAFO .pdf | CV | E-V260083 | 哈萨克斯坦ASIATRAFO | CV | [19 empty] | scanned_or_empty
E-V260084 俄罗斯HMR-SVEL.pdf | CV | E-V260084 | 俄罗斯HMR-SVEL | CV | CVIII-350Y/72.5-10191W |  | III | 350 | Y | 72.5 |  | 10191W | 1 | 63 | 115 | 316 | 334 | 1182 |  | 9 |  |  | CMA7 | ok | type_from_oltc_data
E-V260085 俄罗斯HMR-SVEL.pdf | CV | E-V260085 | 俄罗斯HMR-SVEL | CV | CVIII-350Y/72.5-10191W |  | III | 350 | Y | 72.5 |  | 10191W | 1 | 40 | 115 | 201 | 212 | 1182 |  | 9 |  |  | CMA7 | ok | type_from_oltc_data
E-V260086 俄罗斯HMR-SVEL.pdf | CV | E-V260086 | 俄罗斯HMR-SVEL | CV | CVIII-350Y/72.5-10191W |  | III | 350 | Y | 72.5 |  | 10191W | 1 | 25 | 115 | 126 | 133 | 1182 |  | 9 |  |  | CMA7 | ok | type_from_oltc_data
E-V260087-088 俄罗斯HMR-SVEL.pdf | CV | E-V260087-088 | 俄罗斯HMR-SVEL | CV | [8 empty] | 2 | 16 | 115 |  |  |  |  | 9 |  |  | CMA7 | ok | page_timeout_at_11; no_type
E-V260089 HMPI-台湾-高雄港务局.pdf | CV | E-V260089 | HMPI-台湾-高雄港务局 | CV | [18 empty] | CMA7 | ok | po_not_os; no_type
E-V260090 巴西COMTRAFO.pdf | CV | E-V260090 | 巴西COMTRAFO | CV | CVIII-350D/72.5-10193W |  | III | 350 | D | 72.5 |  | 10193W | 1 | 15 | 69 | 72.5 | 80.5 | 862.5 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-V260091-092乌兹别克斯坦CHIRCHIQ.pdf | CV | E-V260091-092 | 乌兹别克斯坦CHIRCHIQ | CV | [8 empty] | 2 | [10 empty] | ok | po_not_os; no_type
E-V260093-094 俄罗斯HMR-SVEL.pdf | CV | E-V260093-094 | 俄罗斯HMR-SVEL | CV | CVIII-350D/72.5-10193W |  | III | 350 | D | 72.5 |  | 10193W | 2 | 25 | 38.5 | 217 | 230 | 578 |  | 8 |  |  | CMA7 | ok | type_from_oltc_data
E-V260095-096 俄罗斯HMR-SIEMENS.pdf | CV | E-V260095-096 | 俄罗斯HMR-SIEMENS | CV | [8 empty] | 2 | [10 empty] | ok | page_timeout_at_7; no_type
E-V260097 俄罗斯HMR-SVEL.pdf | CV | E-V260097 | 俄罗斯HMR-SVEL | CV | CVIII-350Y/72.5-10191W |  | III | 350 | Y | 72.5 |  | 10191W | 1 | 16 | 115 | 80.3 | 84.9 | 1182 |  | 9 |  |  | CMA7 | ok | type_from_oltc_data
E-V260098-099 印度TOSHIBA.pdf | CV | E-V260098-099 | 印度TOSHIBA | CV | CVIII-350D/72.5-10193G |  | III | 350 | D | 72.5 |  | 10193G | 2 | 24 | [9 empty] | ok | po_not_os; type_from_compact
E-V260100 泰国QTC.pdf | CV | E-V260100 | 泰国QTC | CV | CVIII-350Y/40.5-10193W |  | III | 350 | Y | 40.5 |  | 10193W | 1 | 7.5 | 22 | 196.8 | 218.7 | 158.77 |  | 8 |  |  | SHM-D | ok | type_from_oltc_data
E-V260101 俄罗斯HMR-JSCLP.pdf | CV | E-V260101 | 俄罗斯HMR-JSCLP | CV | [19 empty] | ok | page_timeout_at_8; no_type
E-V260102-103 俄罗斯HMR-SVEL.pdf | CV | E-V260102-103 | 俄罗斯HMR-SVEL | CV | CVIII-350Y/72.5-10193W |  | III | 350 | Y | 72.5 |  | 10193W | 2 | 16 | 35 | 264 | 281 |  |  | 8 |  |  | CMA7 | ok | type_from_oltc_data
E-V260104 巴西COMTRAFO.pdf | CV | E-V260104 | 巴西COMTRAFO | CV | CVIII-350D/72.5-14131W |  | III | 350 | D | 72.5 |  | 14131W | 1 | 12.5 | 69 | 60.39 | 67.09 | 862.5 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-V260105-106 土耳其HMT-Europower.pdf | CV | E-V260105-106 | 土耳其HMT-Europower | CV | CVIII-350D/72.5-10173G |  | III | 350 | D | 72.5 |  | 10173G | 2 | 12.5 | 63 | 66.1 | 71.6 | 693 |  | 7 |  |  | ET-SZ6, CMA7 | ok | type_from_oltc_data
E-V260107 土耳其HMT-Europower.pdf | CV | E-V260107 | 土耳其HMT-Europower | CV | CVIII-350Y/72.5-10173G |  | III | 350 | Y | 72.5 |  | 10173G | 1 | 6.25 | 63 | 57.3 | 62.1 | 400.1 |  | 7 |  |  | ET-SZ6, CMA7 | ok | type_from_oltc_data
E-V260108-109 土耳其HMT-Europower.pdf | CV | E-V260108-109 | 土耳其HMT-Europower | CV | CVIII-350Y/72.5-10173G |  | III | 350 | Y | 72.5 |  | 10173G | 2 | 10 | 63 | 91.6 | 99.3 | 400.1 |  | 7 |  |  | ET-SZ6, CMA7 | ok | type_from_oltc_data
E-V260110-113 土耳其HMT-Europower.pdf | CV | E-V260110-113 | 土耳其HMT-Europower | CV | CVIII-350D/40.5-12231G |  | III | 350 | D | 40.5 |  | 12231G | 4 | 5 | 31.5 | 52.9 | 59.4 | 472.5 |  | 11 |  |  | ET-SZ6, CMA7 | ok | type_from_oltc_data
E-V260114-116 土耳其HMT-Europower.pdf | CV | E-V260114-116 | 土耳其HMT-Europower | CV | CVIII-350Y/40.5-12231G |  | III | 350 | Y | 40.5 |  | 12231G | 3 | 5 | 31.5 | 91.6 | 109.8 | 272.8 |  | 11 |  |  | ET-SZ6, CMA7 | ok | type_from_oltc_data
E-V260117 土耳其HMT-Europower.pdf | CV | E-V260117 | 土耳其HMT-Europower | CV | CVIII-350Y/40.5-12231G |  | III | 350 | Y | 40.5 |  | 12231G | 1 | 10 | 31.5 | 183.3 | 219.5 | 272.8 |  | 11 |  |  | ET-SZ6, CMA7 | ok | type_from_oltc_data
E-V260118 韩国CHERYONG.pdf | CV | E-V260118 | 韩国CHERYONG | CV | 3xCVIII-350Y/72.5-10193W |  | III | 350 | Y | 72.5 | C | 10193W | 3 | 10 |  | 87.5 |  | 1134.5 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-V260119 土耳其HMT-ZTR.pdf | CV | E-V260119 | 土耳其HMT-ZTR | CV | CVIII-350Y/72.5-10191W |  | III | 350 | Y | 72.5 |  | 10191W | 1 | 25 | [9 empty] | ok | po_not_os; type_from_compact
E-V260120-121 土耳其HMT-ZTR.pdf | CV | E-V260120-121 | 土耳其HMT-ZTR | CV | CVIII-350Y/72.5-10191W |  | III | 350 | Y | 72.5 |  | 10191W | 2 | 62 | [9 empty] | ok | po_not_os; type_from_compact
E-V260124-125 俄罗斯HMR-JSHC.pdf | CV | E-V260124-125 | 俄罗斯HMR-JSHC | CV | [8 empty] | 2 | [10 empty] | ok | page_timeout_at_6; no_type
E-V260126-127 哈萨克斯坦ASIATRAFO .pdf | CV | E-V260126-127 | 哈萨克斯坦ASIATRAFO | CV | [8 empty] | 2 | 40 | 115 |  | 239 | 1181.8 |  | 9 |  |  | SHM-D | ok | no_type
E-V260128-129 哈萨克斯坦KENTAU .pdf | CV | E-V260128-129 | 哈萨克斯坦KENTAU | CV | [8 empty] | 2 | [10 empty] | ok | no_type
E-V260130-131 俄罗斯HMR-SVEL.pdf | CV | E-V260130-131 | 俄罗斯HMR-SVEL | CV | CVIII-350Y/72.5-10191W |  | III | 350 | Y | 72.5 |  | 10191W | 2 | 40 | 115 | 201 | 212 | 1182 |  | 9 |  |  | CMA7 | ok | type_from_oltc_data
E-V260132-133 土耳其HMT-BEST.pdf | CV | E-V260132-133 | 土耳其HMT-BEST | CV | CVIII-350D/40.5-10193G |  | III | 350 | D | 40.5 |  | 10193G | 2 | 20 | 34.5 | 193.2 | 227.3 | 431.2 |  |  | 4 | 12 | CMA7 | ok | type_from_oltc_data
E-V260134-135 俄罗斯HMR-SVEL.pdf | CV | E-V260134-135 | 俄罗斯HMR-SVEL | CV | CVIII-350Y/72.5-10193W |  | III | 350 | Y | 72.5 |  | 10193W | 2 | 10 | 35 | 165 | 176 | 303 |  | 8 |  |  | CMA7 | ok | type_from_oltc_data
E-V260136-137 俄罗斯HMR.pdf | CV | E-V260136-137 | 俄罗斯HMR | CV | CVIII-350Y/72.5-10191W |  | III | 350 | Y | 72.5 |  | 10191W | 2 | 63 | 115 | 316 | 334 | 1182 |  | 9 |  |  | CMA7 | ok | type_from_oltc_data
E-V260138-139 哈萨克斯坦KENTAU.pdf | CV | E-V260138-139 | 哈萨克斯坦KENTAU | CV | [8 empty] | 2 | [10 empty] | ok | no_type
E-V260140 俄罗斯HMR-SVEL.pdf | CV | E-V260140 | 俄罗斯HMR-SVEL | CV | CVIII-350Y/72.5-10191W |  | III | 350 | Y | 72.5 |  | 10191W | 1 | 25 | 115 | 126 | 133 | 1182 |  | 9 |  |  | CMA7 | ok | type_from_oltc_data
E-V260141 越南Sanaky.pdf | CV | E-V260141 | 越南Sanaky | CV | CVI-700Y/72.5-10070 | CVI-350/72.5-10070 ¦ CVI-700/72.5-10070 | I | 700 | Y | 72.5 | B | 10070 | 1 | 18.5 |  | 269.27 |  | 769.5 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-V260143 乌兹别克斯坦CHIRCHIQ.pdf | CV | E-V260143 | 乌兹别克斯坦CHIRCHIQ | CV | [19 empty] | ok | po_not_os; no_type
E-V260144 印尼BAMBANG.pdf | CV | E-V260144 | 印尼BAMBANG | CV | [9 empty] | 8 | 20 | 133.33 | 148.15 | 250 |  |  | 8 | 8 | SHM-D, SHM-K | ok | no_type
E-V260145 俄罗斯HMR-SVEL.pdf | CV | E-V260145 | 俄罗斯HMR-SVEL | CV | CVIII-350Y/72.5-10191W |  | III | 350 | Y | 72.5 |  | 10191W | 1 | 25 | 115 | 126 | 133 | 1182 |  | 9 |  |  | CMA7 | ok | type_from_oltc_data
E-V260146-147 俄罗斯HMR-SVEL.pdf | CV | E-V260146-147 | 俄罗斯HMR-SVEL | CV | CVIII-350Y/72.5-10191W |  | III | 350 | Y | 72.5 |  | 10191W | 2 | 40 | 115 | 201 | 212 | 1182 |  | 9 |  |  | CMA7 | ok | type_from_oltc_data
E-V260148-149 俄罗斯HMR-SVEL.pdf | CV | E-V260148-149 | 俄罗斯HMR-SVEL | CV | CVIII-350Y/72.5-10191W |  | III | 350 | Y | 72.5 |  | 10191W | 2 | 63 | 115 | 316 | 334 | 1182 |  | 9 |  |  | CMA7 | ok | type_from_oltc_data
E-V260150 土耳其HMT-MEKSAN.pdf | CV | E-V260150 | 土耳其HMT-MEKSAN | CV | CVIII-350D/40.5-10090 |  | III | 350 | D | 40.5 |  | 10090 | 1 | 15 | 33 | 151.5 | 178.3 | 825 |  |  |  |  | ET-SZ6, CMA7 | ok | type_from_oltc_data
E-V260151 土耳其HMT-ZTR.pdf | CV | E-V260151 | 土耳其HMT-ZTR | CV | SVIII-500D/40.5-10193W |  | III | 500 | D | 40.5 |  | 10193W | 1 | 40 | [9 empty] | ok | po_not_os; type_from_compact
E-V260152 印尼 PT Symphos.pdf | CV | E-V260152 | 印尼 PT Symphos | CV | CVIII-350D/40.5-1 |  | III | 350 | D | 40.5 |  | 1 | 1 | [9 empty] | SHM-D, SHM-K | ok | po_not_os; type_from_compact
E-V260153-154 哈萨克斯坦KENTAU.pdf | CV | E-V260153-154 | 哈萨克斯坦KENTAU | CV | [8 empty] | 2 | [10 empty] | ok | no_type
E-V260155 俄罗斯HMR-SVEL.pdf | CV | E-V260155 | 俄罗斯HMR-SVEL | CV | CVIII-350Y/72.5-10191W |  | III | 350 | Y | 72.5 |  | 10191W | 1 | 15 | 115 | 75 | 80 | 1182 |  | 9 |  |  | CMA7 | ok | type_from_oltc_data
E-V260156-157 俄罗斯HMR-TOGLIATTI.pdf | CV | E-V260156-157 | 俄罗斯HMR-TOGLIATTI | CV | CVIII-350Y/72.5-10191W |  | III | 350 | Y | 72.5 |  | 10191W | 2 | 63 | 115 | 316.3 | 334 | 1182 |  | 9 |  |  | CMA7 | ok | type_from_oltc_data
E-V260158-159 俄罗斯HMR-SVEL.pdf | CV | E-V260158-159 | 俄罗斯HMR-SVEL | CV | CVIII-350Y/72.5-10191W |  | III | 350 | Y | 72.5 |  | 10191W | 2 | 4 | 115 | 20.1 | 21.2 | 1182 |  | 9 |  |  | CMA7 | ok | type_from_oltc_data
E-V260160-161 俄罗斯HMR-SVEL.pdf | CV | E-V260160-161 | 俄罗斯HMR-SVEL | CV | CVIII-350Y/72.5-10193W |  | III | 350 | Y | 72.5 |  | 10193W | 2 | 16 | 36.75 | 251 | 267 | 318 |  | 8 |  |  | CMA7 | ok | type_from_oltc_data
E-V260162 哈萨克斯坦KENTAU.pdf | CV | E-V260162 | 哈萨克斯坦KENTAU | CV | [19 empty] | ok | no_type
E-V260163-164 华明印尼-SYMPHOS.pdf | CV | E-V260163-164 | 华明印尼-SYMPHOS | CV | CVIII-350D/40.5-10193W | CVIII-350D/40.5-1 | III | 350 | D | 40.5 |  | 10193W | 2 |  | 20 | [7 empty] | SHM-D, SHM-K | ok | po_not_os; type_from_compact
E-V260165 哈萨克斯坦KENTAU.pdf | CV | E-V260165 | 哈萨克斯坦KENTAU | CV | [19 empty] | ok | no_type
E-V260166 印尼HMPI 售后.pdf | CV | E-V260166 | 印尼HMPI 售后 | CV | CVIII-350D/40.5-10193W |  | III | 350 | D | 40.5 |  | 10193W | 1 | [10 empty] | ok | po_not_os; type_from_compact
E-V260167-168 意大利SEA.pdf | CV | E-V260167-168 | 意大利SEA | CV | CVIII-350D/40.5-14271W |  | III | 350 | D | 40.5 |  | 14271W | 2 | [9 empty] | CMA7 | ok | po_not_os; type_from_compact
E-V260169 俄罗斯HMR-SVEL.pdf | CV | E-V260169 | 俄罗斯HMR-SVEL | CV | CVIII-350Y/40.5-10193W |  | III | 350 | Y | 40.5 |  | 10193W | 1 | 16 | 36.75 | 251 | 267 | 318 |  | 8 |  |  | CMA7 | ok | type_from_oltc_data
E-V260170-178乌兹别克斯坦CHIRCHIQ.pdf | CV | E-V260170-178 | 乌兹别克斯坦CHIRCHIQ | CV | [8 empty] | 9 | 18 | 36.75 | 300 | 320 | [5 empty] | CMA7 | ok | po_not_os; no_type
E-V260179 土耳其 Taskin Consultancy.pdf | CV | E-V260179 | 土耳其 Taskin Consultancy | CV | [19 empty] | scanned_or_empty
E-V260180 土耳其HMT-SAMI TRAFO.pdf | CV | E-V260180 | 土耳其HMT-SAMI TRAFO | CV | CVIII-350Y/72.5-10090 |  | III | 350 | Y | 72.5 |  | 10090 | 1 | 6.3 | 35 | 103.9 | 114.2 | 454.7 |  | 4 |  |  | ET-SZ6, CMA7 | ok | type_from_oltc_data
E-V260181 俄罗斯HMR-SVEL.pdf | CV | E-V260181 | 俄罗斯HMR-SVEL | CV | CVIII-350Y/72.5-10193W |  | III | 350 | Y | 72.5 |  | 10193W | 1 | 10 | 36.75 | 157 | 167 | 318 |  | 8 |  |  | CMA7 | ok | type_from_oltc_data
E-V260182 俄罗斯HMR-SVEL.pdf | CV | E-V260182 | 俄罗斯HMR-SVEL | CV | CVIII-350Y/72.5-10191W |  | III | 350 | Y | 72.5 |  | 10191W | 1 | 10 | 115 | 50.2 | 53 | 1182 |  | 9 |  |  | CMA7 | ok | type_from_oltc_data
E-V260183-184 俄罗斯HMR-SVEL.pdf | CV | E-V260183-184 | 俄罗斯HMR-SVEL | CV | CVIII-350Y/40.5-10193W |  | III | 350 | Y | 40.5 |  | 10193W | 2 | 16 | 36.75 | 251 | 267 | 318 |  | 8 |  |  | CMA7 | ok | type_from_oltc_data
E-V260185 俄罗斯HMR-SVEL.pdf | CV | E-V260185 | 俄罗斯HMR-SVEL | CV | CVIII-350Y/40.5-10193W |  | III | 350 | Y | 40.5 |  | 10193W | 1 | 16 | 36.75 | 251 | 267 | 318 |  | 8 |  |  | CMA7 | ok | type_from_oltc_data
E-V260186-187 俄罗斯HMR-SVEL.pdf | CV | E-V260186-187 | 俄罗斯HMR-SVEL | CV | CVIII-350Y/72.5-10191W |  | III | 350 | Y | 72.5 |  | 10191W | 2 | 40 | 115 | 201 | 212 | 1182 |  | 9 |  |  | CMA7 | ok | type_from_oltc_data
E-V260188-197 乌兹别克斯坦CHIRCHIQ.pdf | CV | E-V260188-197 | 乌兹别克斯坦CHIRCHIQ | CV | [8 empty] | 10 | 63 | [9 empty] | ok | po_not_os; no_type
E-V260198-199 俄罗斯HMR-SVEL.pdf | CV | E-V260198-199 | 俄罗斯HMR-SVEL | CV | CVIII-350Y/72.5-10191W |  | III | 350 | Y | 72.5 |  | 10191W | 2 | 10 | 115 | 50.2 | 53 | 1182 |  | 9 |  |  | CMA7 | ok | type_from_oltc_data
E-V260200-202 台湾-高雄港务局.pdf | CV | E-V260200-202 | 台湾-高雄港务局 | CV | [8 empty] | 3 | [9 empty] | CMA7 | ok | po_not_os; no_type
E-V260203 阿塞拜疆 ATEF .pdf | CV | E-V260203 | 阿塞拜疆 ATEF | CV | CVIII-350Y/72.5-10191W | CVIII-350Y/72.5-1 | III | 350 | Y | 72.5 |  | 10191W | 1 | 25 | 115 | 125.5 | 149.45 | 1181.84 |  | 9 |  |  | SHM-D | ok | type_from_oltc_data
E-V260204 希腊Hellenic Halyvourgia 售后.pdf | CV | E-V260204 | 希腊Hellenic Halyvourgia 售后 | CV | CVIII-350Y/40.5-12111W |  | III | 350 | Y | 40.5 |  | 12111W | 1 | [10 empty] | ok | po_not_os; type_from_compact
E-V260205-206 巴西COMTRAFO.pdf | CV | E-V260205-206 | 巴西COMTRAFO | CV | CVIII-350D/72.5-10193W |  | III | 350 | D | 72.5 |  | 10193W | 1 | 9.375 | 69 | 45.3 | 50.3 | 862.5 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-V260207-208 俄罗斯HMR-SVEL.pdf | CV | E-V260207-208 | 俄罗斯HMR-SVEL | CV | CVIII-350Y/72.5-10193W |  | III | 350 | Y | 72.5 |  | 10193W | 2 | 10 | 36.75 | 157 | 167 | 318 |  | 8 |  |  | CMA7 | ok | type_from_oltc_data
E-V260209 哈萨克斯坦ASIATRAFO .pdf | CV | E-V260209 | 哈萨克斯坦ASIATRAFO | CV | CVIII-350Y/72.5-10191W |  | III | 350 | Y | 72.5 |  | 10191W | 1 | 25 | 115 |  | 132.6 | 1180 |  | 9 |  |  | CMA7, SHM-D | ok | type_from_os_row
E-V260210-211 俄罗斯HMR-SVEL.pdf | CV | E-V260210-211 | 俄罗斯HMR-SVEL | CV | CVIII-350Y/72.5-10191W |  | III | 350 | Y | 72.5 |  | 10191W | 2 | 25 | 115 | 126 | 133 | 1182 |  | 9 |  |  | CMA7 | ok | type_from_oltc_data
E-V260212-214 哈萨克斯坦ASIATRAFO .pdf | CV | E-V260212-214 | 哈萨克斯坦ASIATRAFO | CV | [8 empty] | 2 | [9 empty] | SHM-D | ok | no_type
E-V260215-216 印尼 Sumbawa.pdf | CV | E-V260215-216 | 印尼 Sumbawa | CV | CVIII-350D/40.5-10193W | CVIII-350D/40.5-1 ¦ CVIII-350D/40.5-2 | III | 350 | D | 40.5 |  | 10193W | 2 | 7.5 | 20 | 216.5 | 333.09 | 500 |  |  | 2 | 14 | SHM-D, SHM-K | ok | type_from_oltc_data
E-V260217-218 哈萨克斯坦ASIATRAFO .pdf | CV | E-V260217-218 | 哈萨克斯坦ASIATRAFO | CV | [8 empty] | 2 | [9 empty] | SHM-D | ok | no_type
E-V260219 哈萨克斯坦ASIATRAFO .pdf | CV | E-V260219 | 哈萨克斯坦ASIATRAFO | CV | [8 empty] | 2 | [9 empty] | SHM-D | ok | no_type
E-V260220 哈萨克斯坦ASIATRAFO .pdf | CV | E-V260220 | 哈萨克斯坦ASIATRAFO | CV | [8 empty] | 2 | [9 empty] | SHM-D | ok | no_type
E-V260221-222 俄罗斯HMR-UETM.pdf | CV | E-V260221-222 | 俄罗斯HMR-UETM | CV | SVIII-500Y/72.5-10193W |  | III | 500 | Y | 72.5 |  | 10193W | 2 | 16 | 22 | 419.9 | 446.7 |  |  | 8 |  |  | CMA7 | ok | type_from_oltc_data
E-V260223 俄罗斯HMR-SVEL.pdf | CV | E-V260223 | 俄罗斯HMR-SVEL | CV | CVIII-350Y/72.5-10191W |  | III | 350 | Y | 72.5 |  | 10191W | 1 | 63 | 115 | 316 | 334 | 1209 |  | 9 |  |  | CMA7, SHM-D | ok | type_from_oltc_data
E-V260224-229 乌兹别克斯坦CHIRCHIQ.pdf | CV | E-V260224-229 | 乌兹别克斯坦CHIRCHIQ | CV | [8 empty] | 6 | [10 empty] | ok | no_type
E-V260230-231 乌兹别克斯坦CHIRCHIQ.pdf | CV | E-V260230-231 | 乌兹别克斯坦CHIRCHIQ | CV | [8 empty] | 2 | [10 empty] | ok | no_type
E-V260232 乌兹别克斯坦CHIRCHIQ.pdf | CV | E-V260232 | 乌兹别克斯坦CHIRCHIQ | CV | [19 empty] | ok | no_type
E-V260233 哈萨克斯坦KENTAU.pdf | CV | E-V260233 | 哈萨克斯坦KENTAU | CV | [19 empty] | ok | no_type
E-V260234 俄罗斯HMR-SVEL.pdf | CV | E-V260234 | 俄罗斯HMR-SVEL | CV | CVIII-350Y/72.5-10193W |  | III | 350 | Y | 72.5 |  | 10193W | 1 | 16 | 36.75 |  |  | 318 |  | 8 |  |  | CMA7 | ok | type_from_oltc_data
E-V260235-236 俄罗斯HMR-SVEL.pdf | CV | E-V260235-236 | 俄罗斯HMR-SVEL | CV | CVIII-350Y/72.5-10191W |  | III | 350 | Y | 72.5 |  | 10191W | 2 | 40 | 115 | 201 | 212 | 1182 |  | 9 |  |  | CMA7 | ok | type_from_oltc_data
E-V260237-238 俄罗斯HMR-UETM.pdf | CV | E-V260237-238 | 俄罗斯HMR-UETM | CV | CVIII-350Y/72.5-10191W |  | III | 350 | Y | 72.5 |  | 10191W | 2 | 25 | 115 | 125.5 | 133 | 1187 |  | 9 |  |  | CMA7 | ok | type_from_oltc_data
E-V260239 华明印尼SYMPHOS.pdf | CV | E-V260239 | 华明印尼SYMPHOS | CV | CVIII-350D/40.5-1 |  | III | 350 | D | 40.5 |  | 1 | 1 | [9 empty] | SHM-D, SHM-K | ok | po_not_os; type_from_compact
E-V260240 华明印尼SYMPHOS.pdf | CV | E-V260240 | 华明印尼SYMPHOS | CV | CVIII-350D/40.5-1 |  | III | 350 | D | 40.5 |  | 1 | 1 | [9 empty] | SHM-D, SHM-K | ok | po_not_os; type_from_compact
E-V260241 俄罗斯HMR-SVEL.pdf | CV | E-V260241 | 俄罗斯HMR-SVEL | CV | CVIII-350Y/72.5-10191W |  | III | 350 | Y | 72.5 |  | 10191W | 1 | 63 | 115 | 316 | 334 | 1182 |  | 9 |  |  | CMA7 | ok | type_from_oltc_data
E-V260242-244 土耳其HMT-Europower.pdf | CV | E-V260242-244 | 土耳其HMT-Europower | CV | CVIII-350D/40.5-14131W |  | III | 350 | D | 40.5 |  | 14131W | 3 | 12.5 | 34.5 | 120.8 | 138.8 | 498.5 |  |  | 3 | 9 | ET-SZ6, CMA7 | ok | type_from_oltc_data
E-V260245-248 印尼GE UNINDO.pdf | CV | E-V260245-248 | 印尼GE UNINDO | CV | CVIII-350Y/72.5-12233W | CVIII-500Y/126-14273W ¦ CVIII-350Y/72.51-2233W ¦ CMIII-500Y/126DE-14273G ¦ CMIII-500Y/126DE-14273W | III | 350 | Y | 72.5 |  | 12233W | 6 | 25 | 60 | 240 | 267.3 | 433 |  |  | 12 | 8 | CMA7 | ok | type_from_oltc_data
E-V260249-250 哈萨克斯坦KENTAU.pdf | CV | E-V260249-250 | 哈萨克斯坦KENTAU | CV | [8 empty] | 2 | [10 empty] | ok | no_type
E-V260251-252 哈萨克斯坦KENTAU.pdf | CV | E-V260251-252 | 哈萨克斯坦KENTAU | CV | [8 empty] | 2 | [9 empty] | SHM-D | ok | no_type
E-V260253-256 哈萨克斯坦KENTAU.pdf | CV | E-V260253-256 | 哈萨克斯坦KENTAU | CV | [8 empty] | 2 |  | 36.75 | [8 empty] | ok | po_not_os; no_type
E-V260257-260 哈萨克斯坦KENTAU.pdf | CV | E-V260257-260 | 哈萨克斯坦KENTAU | CV | [8 empty] | 4 | [10 empty] | ok | no_type
E-V260261-268 乌兹别克斯坦CHIRCHIQ.pdf | CV | E-V260261-268 | 乌兹别克斯坦CHIRCHIQ | CV | [8 empty] | 8 | [10 empty] | ok | no_type
E-V260269 越南HAVEC.pdf | CV | E-V260269 | 越南HAVEC | CV | CVIII-350D/40.5-14271W |  | III | 350 | D | 40.5 |  | 14271W | 1 | 12 | 35 | 197.95 |  | 202 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-V260270 土耳其HMT-MEKSAN.pdf | CV | E-V260270 | 土耳其HMT-MEKSAN | CV | CVIII-350D/40.5-10090 |  | III | 350 | D | 40.5 |  | 10090 | 1 | 7.5 | [8 empty] | ET-SZ6 | ok | page_timeout_at_7; po_not_os; type_from_compact
E-V260271 土耳其HMT-Green Transfo.pdf | CV | E-V260271 | 土耳其HMT-Green Transfo | CV | CVIII-350D/72.5-14271G |  | III | 350 | D | 72.5 |  | 14271G | 1 | 25 | 38 | 219 | 250 | 475 |  |  | 16 | 10 | CMA7 | ok | type_from_oltc_data
E-V260272 土耳其HMT-ZTR.pdf | CV | E-V260272 | 土耳其HMT-ZTR | CV | CVIII-350Y/72.5-10191W |  | III | 350 | Y | 72.5 |  | 10191W | 1 | 6.3 | [8 empty] | HMC-3C | ok | po_not_os; type_from_compact
E-V260273-275 土耳其HMT-ZTR.pdf | CV | E-V260273-275 | 土耳其HMT-ZTR | CV | CVIII-350Y/72.5-10191W |  | III | 350 | Y | 72.5 |  | 10191W | 3 | 40 | [8 empty] | HMC-3C | ok | po_not_os; type_from_compact
E-V260276-277 乌兹别克斯坦CHIRCHIQ.pdf | CV | E-V260276-277 | 乌兹别克斯坦CHIRCHIQ | CV | [8 empty] | 2 | [10 empty] | ok | no_type
E-V260278 俄罗斯HMR-SVEL.pdf | CV | E-V260278 | 俄罗斯HMR-SVEL | CV | CVIII-350Y/72.5-10193W |  | III | 350 | Y | 72.5 |  | 10193W | 1 | 10 | 35 | 165 | 176 | 303 |  | 8 |  |  | CMA7 | ok | type_from_oltc_data
E-V260279 俄罗斯HMR-SVEL.pdf | CV | E-V260279 | 俄罗斯HMR-SVEL | CV | CVIII-350Y/72.5-10191W |  | III | 350 | Y | 72.5 |  | 10191W | 1 | 10 | 115 | 50.2 | 53 | 1182 |  | 9 |  |  | CMA7 | ok | type_from_oltc_data
E-V260280-281 哈萨克斯坦KENTAU.pdf | CV | E-V260280-281 | 哈萨克斯坦KENTAU | CV | [8 empty] | 2 | [6 empty] | 9 |  |  | SHM-D | ok | no_type
E-V260282 俄罗斯HMR-TOGLIATTI.pdf | CV | E-V260282 | 俄罗斯HMR-TOGLIATTI | CV | SVIII-500Y/40.5-10193W |  | III | 500 | Y | 40.5 |  | 10193W | 1 | 25 | 36.75 | 392.8 | 417.8 | 417.8 |  | 8 |  |  | CMA7, SHM-D | ok | type_from_oltc_data
E-V260283-285 哈萨克斯坦KENTAU.pdf | CV | E-V260283-285 | 哈萨克斯坦KENTAU | CV | [8 empty] | 3 | [10 empty] | ok | no_type
E-V260286-289 俄罗斯HMR-SVEL.pdf | CV | E-V260286-289 | 俄罗斯HMR-SVEL | CV | CVIII-350Y/72.5-10193W |  | III | 350 | Y | 72.5 |  | 10193W | 4 | 16 | 36.75 | 251 | 267 | 318 |  | 8 |  |  | CMA7, SHM-D | ok | type_from_oltc_data
E-V260290 泰国QTC.pdf | CV | E-V260290 | 泰国QTC | CV | CVIII-350Y/40.5-12111W |  | III | 350 | Y | 40.5 |  | 12111W | 1 | 8 | 22 | 209.9 | 223.9 | 158.77 |  | 5 |  |  | SHM-D, SHM-K | ok | type_from_oltc_data
E-V260291 越南HAVEC.pdf | CV | E-V260291 | 越南HAVEC | CV | SVIII-500D/40.5-12231W |  | III | 500 | D | 40.5 |  | 12231W | 1 | 15.25 | 22 | 400 |  | 260 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-V260292 俄罗斯HMR-SVEL.pdf | CV | E-V260292 | 俄罗斯HMR-SVEL | CV | CVIII-350Y/72.5-10191W |  | III | 350 | Y | 72.5 |  | 10191W | 1 | 25 | 115 | 126 | 133 | 1182 |  | 9 |  |  | CMA7, SHM-D | ok | type_from_oltc_data
E-V260293 俄罗斯HMR展品.pdf | CV | E-V260293 | 俄罗斯HMR展品 | CV | CVI-350/40.5-10100W | CVI-350/40.5-31 | I | 350 |  | 40.5 |  | 10100W | 1 | [10 empty] | ok | type_from_compact
E-V260294 南非ATM.pdf | CV | E-V260294 | 南非ATM | CV | CVIII-350D/40.5-10090 |  | III | 350 | D | 40.5 |  | 10090 | 2 | 1 | 33 | 10.1 | 11.2 | 825 |  |  |  |  | CMA7 | ok | type_from_compact
E-V260296.pdf | CV | E-V260296 |  | CV | CVIII-350Y/72.5-10191W |  | III | 350 | Y | 72.5 |  | 10191W | 1 | 25 | 115 | 126 | 133 | 1182 |  | 9 |  |  | CMA7 | ok | type_from_oltc_data
E-V260297-300 哈萨克斯坦ASIATRAFO .pdf | CV | E-V260297-300 | 哈萨克斯坦ASIATRAFO | CV | [8 empty] | 2 | [9 empty] | SHM-D | ok | no_type
E-CVT260001.pdf | CVT | E-CVT260001 |  | CVT | CVTIII-160D/12-0909 |  | III | 160 | D | 12 |  | 0909 | 1 | 2.5 | 10 |  | 92.59 | 250 |  | 4 |  |  | HMJK-10Z | ok | type_from_compact
E-CVT260002-005 印度SGB.pdf | CVT | E-CVT260002-005 | 印度SGB | CVT | [8 empty] | 4 |  | 11 | 104.97 | 119.9 | 275 |  |  | 3 | 5 |  | ok | page_timeout_at_9; no_type
E-CVT260006 阿塞拜疆 Hysteresis Group.pdf | CVT | E-CVT260006 | 阿塞拜疆 Hysteresis Group | CVT | CVTIII-200D/12-0909 |  | III | 200 | D | 12 |  | 0909 | 1 |  | 10 | 66.66 | 88.88 | 500 | [5 empty] | ok | type_from_compact
E-CVT260007 印度SGB.pdf | CVT | E-CVT260007 | 印度SGB | CVT | [19 empty] | scanned_or_empty | page_timeout_at_6
E-CZ260001 意大利TMC-Intermagnetic.pdf | CZ | E-CZ260001 | 意大利TMC-Intermagnetic | CZ | 3xCZI-500/40.5-7 |  | I | 500 |  | 40.5 |  | 7 | 3 | 4 | 11.7 | 197 |  |  | 700 |  |  |  | CMA7, HMC-3C | ok | type_from_compact
E-CZ260002-003 土耳其HMT-Beta Transformer.pdf | CZ | E-CZ260002-003 | 土耳其HMT-Beta Transformer | CZ | 3xCZI-500/40.5-9 |  | I | 500 |  | 40.5 |  | 9 | 3 | 5 | 33 | 50.5 | 56.1 | 825 |  |  |  |  | CMA7 | ok | type_from_compact
E-CZ260004 印尼Bambangdjaja.pdf | CZ | E-CZ260004 | 印尼Bambangdjaja | CZ | 3xCZI-500/40.5-17 |  | I | 500 |  | 40.5 |  | 17 | 3 | [9 empty] | ET-SZ6 | ok | po_not_os; type_from_compact
E-CZ260005-006 意大利Intermagnetics.pdf | CZ | E-CZ260005-006 | 意大利Intermagnetics | CZ | 3xCZI-500/40.5-5 |  | I | 500 |  | 40.5 |  | 5 | 3 |  | 35 | 165 | 173.6 | 530 |  | 2 |  |  | CMA7 | ok | type_from_compact
E-CZ260007 意大利FDUEG.pdf | CZ | E-CZ260007 | 意大利FDUEG | CZ | 3xCZI-500/40.5-9 |  | I | 500 |  | 40.5 |  | 9 | 3 | 1 | 33 | 17.5 | 17.5 | 893 |  |  |  |  | CMA7 | ok | type_from_compact
E-CZ260008-009 土耳其HMT-Astor.pdf | CZ | E-CZ260008-009 | 土耳其HMT-Astor | CZ | 3xCZI-500/40.5-17 |  | I | 500 |  | 40.5 |  | 17 | 3 | 2.5 | 33 | 25.3 |  | 375 |  | 8 |  |  | ET-SZ6, CMA7 | ok | type_from_compact
E-CZ260010-011 华明印尼 售后.pdf | CZ | E-CZ260010-011 | 华明印尼 售后 | CZ | [8 empty] | 2 | [10 empty] | ok | no_type
E-CZ260012 德国ABB.pdf | CZ | E-CZ260012 | 德国ABB | CZ | 3xCZI-500/40.5-17 | CVTIII-160/11.5-0909 | I | 500 |  | 40.5 |  | 17 | 3 | 12 | 33 |  |  |  |  | 17 | 8 | 8 | CMA7 | ok | type_from_compact
E-CZ260013-014 俄罗斯HMR-SVEL.pdf | CZ | E-CZ260013-014 | 俄罗斯HMR-SVEL | CZ | [8 empty] | 2 | 6.3 | 35 | 103.92 | 115.47 | 505 |  | 4 |  |  | CMA7 | ok | no_type
E-CZ260015 韩国Hitachi 售后.pdf | CZ | E-CZ260015 | 韩国Hitachi 售后 | CZ | [19 empty] | ok | no_type
E-CZ260016 意大利MF.pdf | CZ | E-CZ260016 | 意大利MF | CZ | 3xCZI-500/40.5-9 |  | I | 500 |  | 40.5 |  | 9 | 3 |  | 20 | 166.3 | 183 | 500 |  |  |  |  | CMA7 | ok | type_from_compact
E-CZ260017-018 俄罗斯HMR-SVEL.pdf | CZ | E-CZ260017-018 | 俄罗斯HMR-SVEL | CZ | [8 empty] | 2 | 6.3 | 35 | 103.92 | 111.89 | 359.69 |  | 4 |  |  | CMA7 | ok | no_type
E-HWV260001 印尼 Bambangdjaja.pdf | HWV | E-HWV260001 | 印尼 Bambangdjaja | HWV | HWVIII-400Y/17.5-18353W |  | III | 400 | Y | 17.5 |  | 18353W | 1 | 1.4 | 13.8 | 117.14 | 117.14 | 431.25 |  | 33 |  |  | CMA7 | ok | type_from_oltc_data
E-HWV260002 意大利TMC-Intermagnetic.pdf | HWV | E-HWV260002 | 意大利TMC-Intermagnetic | HWV | HWVI-800Y/40.5-10193W | HWVI-800/10-18170 | I | 800 | Y | 40.5 |  | 10193W | 1 | 5 | 11 | 350 | 460 |  |  | 8 |  |  | CMA7 | ok | type_from_compact
E-HWV260003 南非 FST.pdf | HWV | E-HWV260003 | 南非 FST | HWV | HWVIII-400D/72.5-18170 |  | III | 400 | D | 72.5 |  | 18170 | 1 | 10 | 66 | 87.48 | 102.9 | 825 |  |  | 4 | 12 |  | ok | type_from_oltc_data
E-HWV260004 土耳其HMT-ZTR.pdf | HWV | E-HWV260004 | 土耳其HMT-ZTR | HWV | HWVIII-800D/40.5-10193W |  | III | 800 | D | 40.5 |  | 10193W | 1 | 40 | [9 empty] | ok | po_not_os; type_from_compact
E-HWV260005 越南HLG.pdf | HWV | E-HWV260005 | 越南HLG | HWV | [9 empty] | 25 | 115 | 125.5 | 149.4 | 1182 |  | 9 |  |  | SHM-D, SHM-K | ok | no_type
E-HWV260006 印尼 Bambangdjaja.pdf | HWV | E-HWV260006 | 印尼 Bambangdjaja | HWV | HWVIII-400Y/17.5-18353W | HWVIII-400Y/40.5-18353W | III | 400 | Y | 17.5 |  | 18353W | 1 | 1.4 | 13.8 | 117.14 | 117.14 | 431.25 |  | 33 |  |  |  | ok | type_from_oltc_data
E-HWV260007-008 华明印尼 SYMPHOS.pdf | HWV | E-HWV260007-008 | 华明印尼 SYMPHOS | HWV | HWVIII-1000D/40.5-1 |  | III | 1000 | D | 40.5 |  | 1 | 2 |  |  | 534.05 | 821.61 |  |  |  | 2 | 14 | CMA7, SHM-K | ok | type_from_compact
E-SHZV260001 澳大利亚 WILSON.pdf | SHZV | E-SHZV260001 | 澳大利亚 WILSON | SHZV | SHZVIII-1000Y/126D-10193W |  | III | 1000 | Y | 126 | D | 10193W | 1 | [10 empty] | ok | po_not_os; type_from_compact
E-SHZV260002 土耳其HMT-BEST.pdf | SHZV | E-SHZV260002 | 土耳其HMT-BEST | SHZV | SHZVIII-600Y/170D-14273G | SHZVIII-600Y/170D-14273W | III | 600 | Y | 170 | D | 14273G | 1 | 180 | 330 | 314.9 | 384.1 | 2857.9 |  | 12 |  |  |  | ok | type_from_oltc_data
E-SHZV260003-009 土耳其HMT-TEIAS库存.pdf | SHZV | E-SHZV260003-009 | 土耳其HMT-TEIAS库存 | SHZV | SHZVIII-1000Y/126D-10183W |  | III | 1000 | Y | 126 | D | 10183W | 7 | 250 |  |  |  |  | 2500 |  | 8 | 7 |  | ok | type_from_oltc_data
E-SHZV260010-013 土耳其HMT-TEIAS库存.pdf | SHZV | E-SHZV260010-013 | 土耳其HMT-TEIAS库存 | SHZV | SHZVIII-1000Y/126D-10183W |  | III | 1000 | Y | 126 | D | 10183W | 4 | 250 |  |  |  |  | 2500 |  | 8 | 7 |  | ok | type_from_oltc_data
E-SHZV260014 印度TOSHIBA.pdf | SHZV | E-SHZV260014 | 印度TOSHIBA | SHZV | [19 empty] | ok | po_not_os; no_type
E-SHZV260015-019 土耳其HMT-Astor.pdf | SHZV | E-SHZV260015-019 | 土耳其HMT-Astor | SHZV | SHZVIII-1000Y/72.5C-10193G |  | III | 1000 | Y | 72.5 | C | 10193G | 5 | 45 | 33 | 787.3 |  | 238.2 |  | 8 |  |  | CMA7 | ok | type_from_oltc_data
E-SHZV260020 意大利GBE.pdf | SHZV | E-SHZV260020 | 意大利GBE | SHZV | [8 empty] | 1 | 16 | 15 | 615.84 |  | 187.5 |  |  |  |  | CMA7 | ok | no_type
E-SHZV260021-022 土耳其HMT-BEST.pdf | SHZV | E-SHZV260021-022 | 土耳其HMT-BEST | SHZV | SHZVIII-600Y/126D-14273G |  | III | 600 | Y | 126 | D | 14273G | 2 | 125 | 400 | 180.4 |  | 2886.8 |  | 12 |  |  |  | ok | page_timeout_at_12; type_from_oltc_data
E-SHZV260023 俄罗斯HMR-SIEMENS.pdf | SHZV | E-SHZV260023 | 俄罗斯HMR-SIEMENS | SHZV | [19 empty] | ok | page_timeout_at_7; no_type
E-SHZV260024-043 土耳其HMT-TASKIN Consultancy.pdf | SHZV | E-SHZV260024-043 | 土耳其HMT-TASKIN Consultancy | SHZV | SHZVIII-1000Y/72.5B-10191W |  | III | 1000 | Y | 72.5 | B | 10191W | 20 | 60 | [9 empty] | ok | po_not_os; type_from_compact
E-SHZV260044-045 土耳其HMT-ASTOR.pdf | SHZV | E-SHZV260044-045 | 土耳其HMT-ASTOR | SHZV | SHZVIII-600Y/126D-14273G |  | III | 600 | Y | 126 | D | 14273G | 2 | 125 | 400 | 180.4 |  | 2886.8 |  | 12 |  |  | SHM-D | ok | type_from_oltc_data
E-SHZV260046-印度TOSHIBA.pdf | SHZV | E-SHZV260046 | 印度TOSHIBA | SHZV | [8 empty] | 1 | [9 empty] | CMA7 | ok | no_type
E-SHZV260047-48 印度TOSHIBA.pdf | SHZV | E-SHZV260047-48 | 印度TOSHIBA | SHZV | SHZVIII-1000Y/72.5B-10193G |  | III | 1000 | Y | 72.5 | B | 10193G | 2 | 40 | [8 empty] | CMA7, SHM-D | ok | po_not_os; type_from_compact
E-SHZV260049 土耳其HMT-BEST.pdf | SHZV | E-SHZV260049 | 土耳其HMT-BEST | SHZV | SHZVIII-1300Y/72.5D-12233G |  | III | 1300 | Y | 72.5 | D | 12233G | 1 | 160 | 120 | 769.8 | 1033.3 | 1039.2 |  |  | 3 | 17 |  | ok | type_from_oltc_data
E-SHZV260050-051 巴西SIEMENS.pdf | SHZV | E-SHZV260050-051 | 巴西SIEMENS | SHZV | SHZVIII-400Y/72.5C-1223 | SHZVIII-400Y/72.5C-12233W | III | 400 | Y | 72.5 | C | 1223 | 2 | 150 | 440 | 196.8 |  | 2540.3 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-SHZV260052-073 土耳其HMT-TEIAS库存.pdf | SHZV | E-SHZV260052-073 | 土耳其HMT-TEIAS库存 | SHZV | SHZVIII-1000Y/126D-10183W |  | III | 1000 | Y | 126 | D | 10183W | 22 | 250 |  |  |  |  | 2500 |  | 8 | 7 |  | ok | page_timeout_at_12; type_from_oltc_data
E-SHZV260074-075 俄罗斯HMR-SVEL.pdf | SHZV | E-SHZV260074-075 | 俄罗斯HMR-SVEL | SHZV | [8 empty] | 2 | 167 | 230 | 1258 | 1321 | 2584 |  | 6 |  |  | CMA7 | ok | no_type
E-SHZV260076-077 巴西DATA.pdf | SHZV | E-SHZV260076-077 | 巴西DATA | SHZV | SHZVIII-600Y/72.5-18353W | SHZVIII-600Y/72.5D-18353W | III | 600 | Y | 72.5 |  | 18353W | 2 | 300 | 500 | 346.4 |  | 1991.9 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-SHZV260079 印度TOSHIBA.pdf | SHZV | E-SHZV260079 | 印度TOSHIBA | SHZV | SHZVIII-1000Y/72.5B-12233W |  | III | 1000 | Y | 72.5 | B | 12233W | 1 | 55 | 132 | [8 empty] | ok | po_not_os; type_from_compact
E-SHZV260080 土耳其HMT-Green Transfo.pdf | SHZV | E-SHZV260080 | 土耳其HMT-Green Transfo | SHZV | SHZVIII-1000Y/126C-14273G |  | III | 1000 | Y | 126 | C | 14273G | 1 | 120 | 110 | 630 | 754 | 952 |  |  | 13 | 11 | CMA7 | ok | type_from_oltc_data
E-SHZV260081 意大利TAMINI.pdf | SHZV | E-SHZV260081 | 意大利TAMINI | SHZV | SHZVIII-1000Y/72.5C-12111W |  | III | 1000 | Y | 72.5 | C | 12111W | 1 | 250 | 400 | [7 empty] | CMA7 | ok | type_from_oltc_data
E-SHZV260082 俄罗斯HMR-SVEL.pdf | SHZV | E-SHZV260082 | 俄罗斯HMR-SVEL | SHZV | [9 empty] | 167 | 230 | 1258 | 1321 | 2584 |  | 6 |  |  | CMA7 | ok | no_type
E-SHZV260083-088 澳大利亚Wilson Transformer.pdf | SHZV | E-SHZV260083-088 | 澳大利亚Wilson Transformer | SHZV | 3xSHZVI-2400Y/72.5D-10193 |  | I | 2400 | Y | 72.5 | D | 10193 | 3 | [10 empty] | ok | po_not_os; type_from_compact
E-SHZV260089-090 巴西WEG.pdf | SHZV | E-SHZV260089-090 | 巴西WEG | SHZV | SHZVIII-1000Y/72.5B-18170 | SHZVIII-1000Y/72.5B-18180 | III | 1000 | Y | 72.5 | B | 18170 | 2 | 10 | 146 | 721.7 | 721.7 | 1157.7 |  |  |  |  | CMA7 | ok | type_from_compact
E-SHZV260091-092 印尼BAMBANG.pdf | SHZV | E-SHZV260091-092 | 印尼BAMBANG | SHZV | [8 empty] | 2 | 165 | 150 | 635.09 | 747.16 | 1299.04 |  |  | 7 | 10 | CMA7 | ok | no_type
E-SHZV260093-094 意大利GETRA-TERNA.pdf | SHZV | E-SHZV260093-094 | 意大利GETRA-TERNA | SHZV | SHZVIII-1000Y/72.5C-12111W | SHZVIII-1000Y/72.5-121110 | III | 1000 | Y | 72.5 | C | 12111W | 2 | 250 | 155 | 570.4 | 673.8 | 191 | 1969 | 5 |  |  | CMA7 | ok | type_from_oltc_data
E-SHZV260095-098 越南EEMC.pdf | SHZV | E-SHZV260095-098 | 越南EEMC | SHZV | SHZVIII-1000Y/72.5C-10193W |  | III | 1000 | Y | 72.5 | C | 10193W | 1 | 200 | 225 | 514 | 571 | 1624 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-SHZV260099-100 意大利GETRA.pdf | SHZV | E-SHZV260099-100 | 意大利GETRA | SHZV | SHZVIII-400Y/252D-14273W | SHZVIII-400/252D-14273W | III | 400 | Y | 252 | D | 14273W | 2 | 63 | 220 | 165.3 | 194.5 | 1588 |  | 12 |  |  | CMA7 | ok | type_from_oltc_data
E-SHZV260101 意大利GETRA.pdf | SHZV | E-SHZV260101 | 意大利GETRA | SHZV | SHZVIII-1000Y/72.5C-12111W | SHZVIII-1000Y/72.5D-12111W | III | 1000 | Y | 72.5 | C | 12111W | 1 | 250 | 135 | 708.3 | 827.1 | 1559 | 2511 | 5 |  |  | CMA7 | ok | type_from_oltc_data
E-SHZV260102 土耳其HMT-BEST.pdf | SHZV | E-SHZV260102 | 土耳其HMT-BEST | SHZV | 3xSHZVI-1200/300D-12111W |  | I | 1200 |  | 300 | D | 12111W | 3 | 250 | 161 | 896.5 | 996.1 | 1860 |  | 5 |  |  |  | ok | type_from_compact
E-SHZV260103 土耳其HMT库存订单.pdf | SHZV | E-SHZV260103 | 土耳其HMT库存订单 | SHZV | SHZVIII-600Y/170D-12233G | SHZVIII-600Y/170DE-12233G | III | 600 | Y | 170 | D | 12233G | 1 | 250 | 420 |  |  |  | 2878 | 10 |  |  |  | ok | type_from_oltc_data
E-SHZV260104 葡萄牙EFACEC.pdf | SHZV | E-SHZV260104 | 葡萄牙EFACEC | SHZV | SHZVIII-1000Y/72.5B-14273W |  | III | 1000 | Y | 72.5 | B | 14273W | 1 | 170 | 150 | 654.3 |  | 866.03 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-SHZV260105 葡萄牙EFACEC.pdf | SHZV | E-SHZV260105 | 葡萄牙EFACEC | SHZV | SHZVIII-1000Y/72.5C-14271W |  | III | 1000 | Y | 72.5 | C | 14271W | 1 | 170 | 220 | 446.1 |  | 1270 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-SHZV260106 印尼PLN.pdf | SHZV | E-SHZV260106 | 印尼PLN | SHZV | SHZVI-1000/126D-10191W |  | I | 1000 |  | 126 | D | 10191W | 1 | [9 empty] | CMA7 | ok | po_not_os; type_from_compact
E-SHZV260107-108 土耳其HMT-BEST.pdf | SHZV | E-SHZV260107-108 | 土耳其HMT-BEST | SHZV | SHZVIII-600Y/126D-14273G |  | III | 600 | Y | 126 | D | 14273G | 2 | 125 | 400 | 180.4 |  | 2886.8 |  | 12 |  |  |  | ok | page_timeout_at_12; type_from_oltc_data
E-SHZV260109-113 土耳其HMT-BEST.pdf | SHZV | E-SHZV260109-113 | 土耳其HMT-BEST | SHZV | SHZVIII-600Y/126D-14273G |  | III | 600 | Y | 126 | D | 14273G | 5 | 125 | 400 | 180.4 |  | 2886.8 |  | 12 |  |  |  | ok | page_timeout_at_12; type_from_oltc_data
E-SHZV260114 意大利TIRONI.pdf | SHZV | E-SHZV260114 | 意大利TIRONI | SHZV | [8 empty] | 1 | 125 |  | 546.7 |  | 1524.2 |  |  |  |  | CMA7 | ok | no_type
E-SHZV260116 土耳其HMT-TEIAS库存.pdf | SHZV | E-SHZV260116 | 土耳其HMT-TEIAS库存 | SHZV | SHZVIII-600Y/126D-14273G |  | III | 600 | Y | 126 | D | 14273G | 1 | 125 | 400 | 180.4 |  | 2886.8 |  | 12 |  |  |  | ok | page_timeout_at_12; type_from_oltc_data
E-SHZV260117-119 土耳其HMT-TASKIN Consultancy.pdf | SHZV | E-SHZV260117-119 | 土耳其HMT-TASKIN Consultancy | SHZV | SHZVIII-1000Y/72.5B-10191W |  | III | 1000 | Y | 72.5 | B | 10191W | 3 | 60 | [8 empty] | CMA7 | ok | type_from_oltc_data
E-SHZV260120-125 土耳其HMT-BEST.pdf | SHZV | E-SHZV260120-125 | 土耳其HMT-BEST | SHZV | SHZVIII-600Y/126D-14273G |  | III | 600 | Y | 126 | D | 14273G | 6 | 125 | 400 | 180.4 |  | 2886.8 |  | 12 |  |  |  | ok | page_timeout_at_12; type_from_oltc_data
E-SHZV260129-130 印尼UNINDO.pdf | SHZV | E-SHZV260129-130 | 印尼UNINDO | SHZV | SHZVIII-1000Y/72.5B-12111W | SHZVIII-1000Y/72.5D-12110W | III | 1000 | Y | 72.5 | B | 12111W | 2 | 130 | 132 | 568.6 | 631.8 | 1905 |  |  | 6 | 4 | CMA7 | ok | type_from_oltc_data
E-SHZV260131 印尼BAMBANGDJAJA.pdf | SHZV | E-SHZV260131 | 印尼BAMBANGDJAJA | SHZV | SHZVIII-1000Y/72.5B-18353W |  | III | 1000 | Y | 72.5 | B | 18353W | 1 | 15.8 | 13.8 | 661.02 | 734.47 | 49.796 |  | 16 |  |  | CMA7 | ok | type_from_oltc_data
E-SHZV260132 澳大利亚 Wilson Transformer.pdf | SHZV | E-SHZV260132 | 澳大利亚 Wilson Transformer | SHZV | SHZVIII-1000Y/170D-12233W |  | III | 1000 | Y | 170 | D | 12233W | 1 | 240 | 220 | 629.9 | 720 | 1588 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-SHZV260133 印尼HMPI 型式试验.pdf | SHZV | E-SHZV260133 | 印尼HMPI 型式试验 | SHZV | [19 empty] | scanned_or_empty
E-S260001-002 哈萨克斯坦KENTAU.pdf | SY | E-S260001-002 | 哈萨克斯坦KENTAU | SY | SYXZZ-40.5-200-9 | CVIII-350Y/72.5-10191W |  | 200 |  | 40.5 |  | 9 | 2 | [10 empty] | ok | type_from_sy
E-S260003-008 哈萨克斯坦KENTAU.pdf | SY | E-S260003-008 | 哈萨克斯坦KENTAU | SY | SYXZZ-40.5-200-9 | CVIII-350Y/72.5-10191W |  | 200 |  | 40.5 |  | 9 | 6 | [10 empty] | ok | type_from_sy
E-S260009-018 哈萨克斯坦KENTAU.pdf | SY | E-S260009-018 | 哈萨克斯坦KENTAU | SY | SYXZZ-40.5-200-9 | CVIII-350Y/72.5-10191W |  | 200 |  | 40.5 |  | 9 | 10 | [10 empty] | ok | po_not_os; type_from_sy
E-S260019-028 哈萨克斯坦KENTAU.pdf | SY | E-S260019-028 | 哈萨克斯坦KENTAU | SY | SYXZZ-40.5-200-9 | CVIII-350Y/72.5-10191W |  | 200 |  | 40.5 |  | 9 | 10 | [9 empty] | SHM-D | ok | type_from_sy
E-S260029 俄罗斯HMR-SVEL.pdf | SY | E-S260029 | 俄罗斯HMR-SVEL | SY | SYXZZ-40.5-20-0 |  |  | 20 |  | 40.5 |  | 0 | 1 | 6.3 | 35 | 104 | 109.5 | 505 |  | 4 |  |  | HMBK-35 | ok | type_from_oltc_data
E-S260029.pdf | SY | E-S260029 |  | SY | SYXZZ-40.5-20-0 |  |  | 20 |  | 40.5 |  | 0 | 1 | 6.3 | 35 | 104 | 109.5 | 505 |  | 4 |  |  | HMBK-35 | ok | type_from_oltc_data
E-S260030-031 俄罗斯HMR-SVEL.pdf | SY | E-S260030-031 | 俄罗斯HMR-SVEL | SY | SYXZZ-40.5-20-0 |  |  | 20 |  | 40.5 |  | 0 | 2 | 6.3 | 35 | 104 | 109 | 505 |  | 4 |  |  | HMBK-35 | ok | type_from_oltc_data
E-S260032-033 乌兹别克斯坦CHIRCHIQ.pdf | SY | E-S260032-033 | 乌兹别克斯坦CHIRCHIQ | SY | WDGV-800/40.5-6x5 |  | V | 800 |  | 40.5 |  | 6x5 | 2 | 6.3 | 36.75 | [5 empty] | 4 | 4 |  | ok | type_from_compact
E-S260034 懋实特.pdf | SY | E-S260034 | 懋实特 | SY | [19 empty] | scanned_or_empty
E-S260035-036 上海法乐琦.pdf | SY | E-S260035-036 | 上海法乐琦 | SY | SYXZZ-40.5-20-0 |  |  | 20 |  | 40.5 |  | 0 | 2 | 2.5 | 35 | 41.2 | 45.8 | 510 |  | 4 |  |  | HMBK-35 | ok | type_from_oltc_data
E-S260037-038 上海法乐琦.pdf | SY | E-S260037-038 | 上海法乐琦 | SY | SYXZZ-40.5-20-0 |  |  | 20 |  | 40.5 |  | 0 | 2 | 4 | 35 | 66 | 73.3 | 510 |  | 4 |  |  | HMBK-35 | ok | type_from_oltc_data
E-S260039-040 上海法乐琦.pdf | SY | E-S260039-040 | 上海法乐琦 | SY | SYXZZ-40.5-20-0 |  |  | 20 |  | 40.5 |  | 0 | 2 | 6.3 | 35 | 104 | 115.5 | 510 |  | 4 |  |  | HMBK-35 | ok | type_from_oltc_data
E-S260041-050 哈萨克斯坦KENTAU.pdf | SY | E-S260041-050 | 哈萨克斯坦KENTAU | SY | [8 empty] | 10 | [10 empty] | ok | no_type
E-S260051-053乌兹别克斯坦CHIRCHIQ.pdf | SY | E-S260051-053 | 乌兹别克斯坦CHIRCHIQ | SY | CVIII-350Y/40.5-10193W |  | III | 350 | Y | 40.5 |  | 10193W | 3 | [10 empty] | ok | type_from_compact
E-S260054-063 哈萨克斯坦KENTAU .pdf | SY | E-S260054-063 | 哈萨克斯坦KENTAU | SY | [8 empty] | 10 | [10 empty] | ok | no_type
E-S260064-065 哈萨克斯坦KENTAU.pdf | SY | E-S260064-065 | 哈萨克斯坦KENTAU | SY | [8 empty] | 2 | [10 empty] | ok | no_type
E-S260066 乌兹别克斯坦CHIRCHIQ.pdf | SY | E-S260066 | 乌兹别克斯坦CHIRCHIQ | SY | CVIII-350Y/72.5-10191W |  | III | 350 | Y | 72.5 |  | 10191W | 1 | [10 empty] | ok | type_from_compact
E-S260067-074 乌兹别克斯坦CHIRCHIQ.pdf | SY | E-S260067-074 | 乌兹别克斯坦CHIRCHIQ | SY | [8 empty] | 8 | [10 empty] | ok | no_type
E-CM2260001-002 意大利TIRONI.pdf | VCM | E-CM2260001-002 | 意大利TIRONI | CM2 | CM2III-500Y/72.5C-12233G |  | III | 500 | Y | 72.5 | C | 12233G | 2 | [10 empty] | ok | type_from_compact
E-CM2260003-004 意大利GETRA-ENEL.PDF | VCM | E-CM2260003-004 | 意大利GETRA-ENEL | CM2 | CM2III-500Y/170B-14273G |  | III | 500 | Y | 170 | B | 14273G | 2 | [9 empty] | CMA7 | ok | po_not_os; type_from_compact
E-CM2260005-008 意大利GETRA-ENEL.PDF | VCM | E-CM2260005-008 | 意大利GETRA-ENEL | CM2 | CM2III-500Y/170B-14273G |  | III | 500 | Y | 170 | B | 14273G | 4 | [9 empty] | CMA7 | ok | po_not_os; type_from_compact
E-CM2260009 意大利GETRA-TERNA.PDF | VCM | E-CM2260009 | 意大利GETRA-TERNA | CM2 | CM2III-500Y/170B-18171W |  | III | 500 | Y | 170 | B | 18171W | 1 | [9 empty] | CMA7 | ok | po_not_os; type_from_compact
E-CM2260010 越南EEMC.pdf | VCM | E-CM2260010 | 越南EEMC | CM2 | CM2III-500Y/72.5B-10193W |  | III | 500 | Y | 72.5 | B | 10193W | 1 | 63 | 225 |  | 179.62 | 1624 |  | 8 |  |  |  | ok | type_from_oltc_data
E-CM2260011-012 美国HMUS-VIRGINIA.pdf | VCM | E-CM2260011-012 | 美国HMUS-VIRGINIA | CM2 | CM2I-500/252D-18353W |  | I | 500 |  | 252 | D | 18353W | 2 | 75 | 230 | 65 |  | 1471 |  |  |  |  | CMA7 | ok | po_not_os; type_from_compact
E-CM2260013-032 土耳其HMT-CM2散件.pdf | VCM | E-CM2260013-032 | 土耳其HMT-CM2散件 | CM2 | CM2III-600Y/72.5C-14273G |  | III | 600 | Y | 72.5 | C | 14273G | 20 | 62.5 | 154 | 234.3 |  | 1111.4 |  | 12 |  |  | SHM-D | ok | type_from_oltc_data
E-CM2260033-067 土耳其HMT-CM2散件.pdf | VCM | E-CM2260033-067 | 土耳其HMT-CM2散件 | CM2 | CM2III-600Y/72.5C-14273G |  | III | 600 | Y | 72.5 | C | 14273G | 35 | 62.5 | 154 | 234.3 |  | 1111.4 |  | 12 |  |  | SHM-D | ok | type_from_oltc_data
E-CM2260068-112 土耳其HMT-CM2散件.pdf | VCM | E-CM2260068-112 | 土耳其HMT-CM2散件 | CM2 | CM2III-600Y/72.5C-14273G |  | III | 600 | Y | 72.5 | C | 14273G | 45 | 100 | 154 | 374.9 |  | 1111.4 |  | 12 |  |  | SHM-D | ok | type_from_oltc_data
E-CM2260113 秘鲁Delcrosa.pdf | VCM | E-CM2260113 | 秘鲁Delcrosa | CM2 | CM2III-500Y/72.5B-14271W |  | III | 500 | Y | 72.5 | B | 14271W | 1 | 25 | 58 | 248.86 |  | 565 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CM2260115-116 印尼 Bambangdjaja.pdf | VCM | E-CM2260115-116 | 印尼 Bambangdjaja | CM2 | [8 empty] | 4 | 65 | 150 | 254 | 294.34 | 1299.04 |  |  | 7 | 10 | CMA7 | ok | no_type
E-CM2260117 秘鲁DELCROSA.pdf | VCM | E-CM2260117 | 秘鲁DELCROSA | CM2 | CM2III-500Y/72.5B-14271W |  | III | 500 | Y | 72.5 | B | 14271W | 1 | 25 | 66 | 218.69 |  | 381.05 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CM2260118 意大利TRAFOSER.pdf | VCM | E-CM2260118 | 意大利TRAFOSER | CM2 | CM2III-300Y/170B-12233W | CM2III-500Y/170B-1 | III | 300 | Y | 170 | B | 12233W | 1 | 20 | 150 | 77 | 88 | 1082.5 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CM2260119 俄罗斯HMR-SIEMENS.pdf | VCM | E-CM2260119 | 俄罗斯HMR-SIEMENS | CM2 | [8 empty] | 1 | [9 empty] | CMA7 | ok | no_type
E-CM2260120 俄罗斯HMR-SIEMENS.pdf | VCM | E-CM2260120 | 俄罗斯HMR-SIEMENS | CM2 | 3xCM2I-1500/72.5B-10193W |  | I | 1500 |  | 72.5 | B | 10193W | 3 | 80 | 24 |  |  | 360 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CM2260121 俄罗斯HMR-TOGLIATTI.pdf | VCM | E-CM2260121 | 俄罗斯HMR-TOGLIATTI | CM2 | CM2III-500Y/72.5C-14273W |  | III | 500 | Y | 72.5 | C | 14273W | 1 | 100 | 230 | 251 | 264.2 | 1328 |  | 12 |  |  | CMA7 | ok | type_from_oltc_data
E-CM2260122 俄罗斯HMR-TOGLIATTI.pdf | VCM | E-CM2260122 | 俄罗斯HMR-TOGLIATTI | CM2 | CM2III-500Y/72.5C-14273W |  | III | 500 | Y | 72.5 | C | 14273W | 1 | 63 | 230 | 158.1 | 166.5 | 1328 |  | 12 |  |  | CMA7 | ok | type_from_oltc_data
E-CM2260123-124 南非ACTOM.pdf | VCM | E-CM2260123-124 | 南非ACTOM | CM2 | [8 empty] | 2 | 31.5 | 132 | 137.8 | 162.1 | 952.6 |  |  |  |  | CMA7 | ok | no_type
E-CM2260125-126 意大利GETRA-ENEL.PDF | VCM | E-CM2260125-126 | 意大利GETRA-ENEL | CM2 | CM2III-500Y/170B-14273G | CM2III-500Y/170B-1427 | III | 500 | Y | 170 | B | 14273G | 2 | [9 empty] | CMA7 | ok | po_not_os; type_from_compact
E-CM2260127-136 土耳其HMT-CM2库存.pdf | VCM | E-CM2260127-136 | 土耳其HMT-CM2库存 | CM2 | CM2III-600Y/72.5C-14273G |  | III | 600 | Y | 72.5 | C | 14273G | 10 | 100 | 154 | 374.9 |  | 1111.4 |  | 12 |  |  | SHM-D | ok | type_from_oltc_data
E-CM2260137-138 意大利GETRA-ENEL.pdf | VCM | E-CM2260137-138 | 意大利GETRA-ENEL | CM2 | CM2III-500Y/126B-14273G |  | III | 500 | Y | 126 | B | 14273G | 2 | 25 | 132 | 109.3 | 128.6 | 953 |  | 12 |  |  | CMA7 | ok | type_from_oltc_data
E-CM2260139 捷克Revos-ZREW.pdf | VCM | E-CM2260139 | 捷克Revos-ZREW | CM2 | CM2III-500Y/126B-12231W |  | III | 500 | Y | 126 | B | 12231W | 1 | 63 | 115 | 316.3 | 355.4 | 664 |  | 11 |  |  | CMA7 | ok | type_from_oltc_data
E-CM2260140 俄罗斯HMR-SVEL.pdf | VCM | E-CM2260140 | 俄罗斯HMR-SVEL | CM2 | CM2III-500Y/72.5C-14273W |  | III | 500 | Y | 72.5 | C | 14273W | 1 | 160 | 230 | 402 | 423 | 1328 |  | 12 |  |  | CMA7 | ok | type_from_oltc_data
E-CM2260141 俄罗斯HMR-SVEL.pdf | VCM | E-CM2260141 | 俄罗斯HMR-SVEL | CM2 | 3xCM2I-1500/170B-14131W |  | I | 1500 |  | 170 | B | 14131W | 3 | 250 | 121 | 1193 | 1356 | 1346 |  | 6 |  |  | CMA7 | ok | type_from_oltc_data
E-CM2260142-143 葡萄牙EFACEC.pdf | VCM | E-CM2260142-143 | 葡萄牙EFACEC | CM2 | CM2I-600/72.5C-12233W |  | I | 600 |  | 72.5 | C | 12233W | 2 | 16 | 63 |  | 290.9 | 800 |  | 10 |  |  | CMA7 | ok | type_from_oltc_data
E-CM2260144 秘鲁Delcrosa.pdf | VCM | E-CM2260144 | 秘鲁Delcrosa | CM2 | CM2III-500Y/72.5B-14271W |  | III | 500 | Y | 72.5 | B | 14271W | 1 | 15 | 53 | 163.4 |  | 306 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CM2260145 意大利GETRA.pdf | VCM | E-CM2260145 | 意大利GETRA | CM2 | CM2III-500Y/72.5B-14273G | CM2II-500Y/72.5B-14273G | III | 500 | Y | 72.5 | B | 14273G | 1 | 40 | 60 | 385 | 453 | 433 |  | 12 |  |  | CMA7 | ok | type_from_oltc_data
E-CM2260146-148 意大利GETRA.pdf | VCM | E-CM2260146-148 | 意大利GETRA | CM2 | CM2III-500Y/170B-14273G |  | III | 500 | Y | 170 | B | 14273G | 3 | [9 empty] | CMA7 | ok | po_not_os; type_from_compact
E-CM2260149-150 缅甸PTE.pdf | VCM | E-CM2260149-150 | 缅甸PTE | CM2 | CM2III-500Y/170D-12233W |  | III | 500 | Y | 170 | D | 12233W | 1 | [10 empty] | ok | po_not_os; type_from_compact
E-CM2260151 越南-青岛柏沐宸 售后.pdf | VCM | E-CM2260151 | 越南-青岛柏沐宸 售后 | CM2 | 3xCM2I-1500/72.5C-16160 |  | I | 1500 |  | 72.5 | C | 16160 | 3 | 150 | 35 |  | 1429 |  | 1832 |  |  |  | CMA7 | ok | type_from_oltc_data
E-CM2260152 俄罗斯HMR-SIEMENS.pdf | VCM | E-CM2260152 | 俄罗斯HMR-SIEMENS | CM2 | CM2III-600Y/72.5B-10191W |  | III | 600 | Y | 72.5 | B | 10191W | 1 | 100 | 115 | 502 | 530 | 1181 |  | 9 |  |  | CMA7 | ok | type_from_oltc_data
E-CM2260153 俄罗斯HMR-SIEMENS.pdf | VCM | E-CM2260153 | 俄罗斯HMR-SIEMENS | CM2 | [19 empty] | ok | page_timeout_at_8; no_type
E-CM2260154 印尼华明XD SAKTI.pdf | VCM | E-CM2260154 | 印尼华明XD SAKTI | CM2 | CM2III-500Y/126C-10193W |  | III | 500 | Y | 126 | C | 10193W | 1 | 30 | [9 empty] | ok | po_not_os; type_from_compact
E-CM2260155-157 印尼PLN.pdf | VCM | E-CM2260155-157 | 印尼PLN | CM2 | CM2I-600Y/170C-12233W | CM2I-600Y/170-12233W | I | 600 | Y | 170 | C | 12233W | 1 | 83.3 |  | 525 | 591.4 | 1985 |  | 9 |  |  | CMA7 | ok | type_from_oltc_data
E-CM2260158 华明印尼XD SAKTI.pdf | VCM | E-CM2260158 | 华明印尼XD SAKTI | CM2 | CM2III-500Y/126C-10193W |  | III | 500 | Y | 126 | C | 10193W | 1 | 45 | [9 empty] | ok | po_not_os; type_from_compact
E-CM2260159 土耳其HMT-Astor.pdf | VCM | E-CM2260159 | 土耳其HMT-Astor | CM2 | CM2III-500Y/170C-12233G |  | III | 500 | Y | 170 | C | 12233G | 1 | 60 | 150 | 230.9 | 271.7 | 1299 |  | 10 |  |  | CMA7 | ok | type_from_oltc_data
E-CM2260160-164 意大利NEWTON.pdf | VCM | E-CM2260160-164 | 意大利NEWTON | CM2 | CM2III-500Y/170C-14273W |  | III | 500 | Y | 170 | C | 14273W | 5 | [9 empty] | ET-SZ6 | ok | po_not_os; type_from_compact
E-CM2260165-167 意大利NEWTON.pdf | VCM | E-CM2260165-167 | 意大利NEWTON | CM2 | CM2III-500Y/170C-14273W |  | III | 500 | Y | 170 | C | 14273W | 3 | [9 empty] | ET-SZ6 | ok | po_not_os; type_from_compact
E-CM2260168 巴西WEG.pdf | VCM | E-CM2260168 | 巴西WEG | CM2 | CM2III-500Y/72.5C-18353W |  | III | 500 | Y | 72.5 | C | 18353W | 1 | 95 | 230 | 238.47 |  | 1437.5 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CM2260169 俄罗斯HMR-DELTA.pdf | VCM | E-CM2260169 | 俄罗斯HMR-DELTA | CM2 | [19 empty] | scanned_or_empty
E-CM2260170 韩国Hyosung Changwon.pdf | VCM | E-CM2260170 | 韩国Hyosung Changwon | CM2 | CM2III-500Y/72.5B-18353W |  | III | 500 | Y | 72.5 | B | 18353W | 1 | [9 empty] | CMA7 | ok | po_not_os; type_from_compact
E-CM2260171-180 土耳其HMT-CM2散件.pdf | VCM | E-CM2260171-180 | 土耳其HMT-CM2散件 | CM2 | CM2III-600Y/72.5C-14273G |  | III | 600 | Y | 72.5 | C | 14273G | 10 | 100 | 154 | 374.9 |  | 1111.4 |  | 12 |  |  | SHM-D | ok | type_from_oltc_data
E-CM2260181 意大利Trafoser.pdf | VCM | E-CM2260181 | 意大利Trafoser | CM2 | CM2III-300Y/170B-10191W | CM2III-500Y/170B-1 | III | 300 | Y | 170 | B | 10191W | 1 | 25 | 150 | 96.2 | 109.3 | 1995 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CM2260182 俄罗斯HMR-SIEMENS.pdf | VCM | E-CM2260182 | 俄罗斯HMR-SIEMENS | CM2 | [19 empty] | ok | page_timeout_at_7; no_type
E-CM2260183 意大利TIRONI.pdf | VCM | E-CM2260183 | 意大利TIRONI | CM2 | CM2III-500Y/126D-14271G |  | III | 500 | Y | 126 | D | 14271G | 1 | 125 | [8 empty] | CMA7 | ok | po_not_os; type_from_compact
E-CM2260184-203 土耳其HMT-CM2散件.pdf | VCM | E-CM2260184-203 | 土耳其HMT-CM2散件 | CM2 | CM2III-600Y/72.5C-14273G |  | III | 600 | Y | 72.5 | C | 14273G | 20 | 100 | 154 | 374.9 |  | 1111.4 |  | 12 |  |  | SHM-D | ok | type_from_oltc_data
E-CM2260204 俄罗斯HMR-JSHC.pdf | VCM | E-CM2260204 | 俄罗斯HMR-JSHC | CM2 | CM2III-500Y/72.5B-10191W |  | III | 500 | Y | 72.5 | B | 10191W | 1 | 80 | 115 | 401.6 | 424.2 | 1182 |  | 9 |  |  | CMA7 | ok | type_from_oltc_data
E-CM2260205 俄罗斯HMR-SIEMENS.pdf | VCM | E-CM2260205 | 俄罗斯HMR-SIEMENS | CM2 | [19 empty] | ok | page_timeout_at_7; no_type
E-CM2260206 南非ACTOM.pdf | VCM | E-CM2260206 | 南非ACTOM | CM2 | [8 empty] | 2 | 25 | 66 | 218.7 | 257.3 | 476.3 |  |  |  |  | CMA7 | ok | no_type
E-CM2260207 意大利TAMINI.pdf | VCM | E-CM2260207 | 意大利TAMINI | CM2 | CM2III-600Y/170B-12233W |  | III | 600 | Y | 170 | B | 12233W | 1 | 115 | 150 | 442.7 | 505.9 | 1082 | [5 empty] | ok | type_from_oltc_data
E-CM2260208 俄罗斯HMR-SVEL.pdf | VCM | E-CM2260208 | 俄罗斯HMR-SVEL | CM2 | [19 empty] | ok | page_timeout_at_7; no_type
E-CM2260209 俄罗斯HMR-SVEL.pdf | VCM | E-CM2260209 | 俄罗斯HMR-SVEL | CM2 | [19 empty] | ok | page_timeout_at_7; no_type
E-CM2260210-213 俄罗斯HMR.pdf | VCM | E-CM2260210-213 | 俄罗斯HMR | CM2 | CM2I-1500/170D-22433W |  | I | 1500 |  | 170 | D | 22433W | 1 | 333 |  | 980 | 1030 | [5 empty] | CMA7 | ok | type_from_oltc_data
E-CM2260214-219 印尼 Bambangdjaja.pdf | VCM | E-CM2260214-219 | 印尼 Bambangdjaja | CM2 | CM2III-500Y/72.5B-10181W |  | III | 500 | Y | 72.5 | B | 10181W | 4 | 65 | 150 | 254 | 294.34 | 1299.04 |  |  | 7 | 10 | CMA7 | ok | type_from_compact
E-CM2260220-222 意大利NEWTON.pdf | VCM | E-CM2260220-222 | 意大利NEWTON | CM2 | CM2III-500Y/72.5B-14273G |  | III | 500 | Y | 72.5 | B | 14273G | 3 | 5.76 | [8 empty] | ET-SZ6 | ok | po_not_os; type_from_compact
E-CM2260223 哥伦比亚Commercial explore.pdf | VCM | E-CM2260223 | 哥伦比亚Commercial explore | CM2 | [8 empty] | 1 | 25 | 110 | 131 |  | 915 |  |  |  |  | CMA7 | ok | no_type
E-CM2260224-225 印度TOSHIBA.pdf | VCM | E-CM2260224-225 | 印度TOSHIBA | CM2 | CM2III-600Y/72.5B-10193W |  | III | 600 | Y | 72.5 | B | 10193W | 2 | 60 | [8 empty] | CMA7 | ok | po_not_os; type_from_compact
E-CM2260226-227 俄罗斯HMR-SVEL.pdf | VCM | E-CM2260226-227 | 俄罗斯HMR-SVEL | CM2 | 3xCM2I-1500/170B-14131W |  | I | 1500 |  | 170 | B | 14131W | 3 | 250 | 230 | 1193 | 1356 | 1346 |  | 6 |  |  | CMA7 | ok | type_from_oltc_data
E-CM2260228 意大利NEWTON.pdf | VCM | E-CM2260228 | 意大利NEWTON | CM2 | CM2III-500Y/72.5B-14273G |  | III | 500 | Y | 72.5 | B | 14273G | 1 | [9 empty] | ET-SZ6 | ok | po_not_os; type_from_compact
E-CM2260229 土耳其HMT-Imefy.pdf | VCM | E-CM2260229 | 土耳其HMT-Imefy | CM2 | CM2III-600Y/72.5B-12231G |  | III | 600 | Y | 72.5 | B | 12231G | 1 | 40 | 66 | 349.91 |  | 571.58 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CM2260230 意大利Trafoser.pdf | VCM | E-CM2260230 | 意大利Trafoser | CM2 | CM2III-500Y/170B-12233W |  | III | 500 | Y | 170 | B | 12233W | 1 | 40 | 150 | 154 | 181.1 | 1875 |  |  |  |  | SHM-D, SHM-K | ok | type_from_oltc_data
E-CM2260231-232 俄罗斯HMR-TOGLIATTI.pdf | VCM | E-CM2260231-232 | 俄罗斯HMR-TOGLIATTI | CM2 | CM2III-500Y/72.5B-14273W |  | III | 500 | Y | 72.5 | B | 14273W | 2 | 40 | 230 | 100.41 | 104.59 | 1328 |  | 12 |  |  | CMA7 | ok | type_from_oltc_data
E-CM2260233-236 俄罗斯HMR-JSHC.pdf | VCM | E-CM2260233-236 | 俄罗斯HMR-JSHC | CM2 | CM2III-500Y/72.5B-10191W |  | III | 500 | Y | 72.5 | B | 10191W | 4 | 80 | 115 | 401.6 | 424.2 |  |  | 9 |  |  | CMA7 | ok | type_from_oltc_data
E-CM2260237 意大利TAMINI.pdf | VCM | E-CM2260237 | 意大利TAMINI | CM2 | CM2III-500Y/170B-12233W |  | III | 500 | Y | 170 | B | 12233W | 1 | 0.11 | 150 | 423.4 |  | 1082.5 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CM2260238 意大利Trafoser.pdf | VCM | E-CM2260238 | 意大利Trafoser | CM2 | CM2III-300Y/170B-12233W | CM2III-500Y/170B-1 | III | 300 | Y | 170 | B | 12233W | 1 | 33 | 132 | 144.3 |  | 952 |  |  |  |  | CMA7, SHM-D, SHM-K | ok | type_from_oltc_data
E-CM2260239 意大利GETRA.pdf | VCM | E-CM2260239 | 意大利GETRA | CM2 | [18 empty] | CMA7 | ok | page_timeout_at_11; po_not_os; no_type
E-CM2260240-249 土耳其HMT-CM2散件.pdf | VCM | E-CM2260240-249 | 土耳其HMT-CM2散件 | CM2 | CM2III-600Y/72.5C-14273G |  | III | 600 | Y | 72.5 | C | 14273G | 10 | 62.5 | 154 | 234.3 |  | 1111.4 |  | 12 |  |  | SHM-D | ok | type_from_oltc_data
E-CM2260250-256 印度T&R.pdf | VCM | E-CM2260250-256 | 印度T&R | CM2 | CM2I-500D/72.5B-14273W | CM2I-500/72.5B-14273W | I | 500 | D | 72.5 | B | 14273W | 7 | 6 | 33 | 176 |  | 929.6 |  |  |  |  | CMA7, SHM-D | ok | type_from_oltc_data
E-CM2260257 土耳其HMT-BETA.pdf | VCM | E-CM2260257 | 土耳其HMT-BETA | CM2 | CM2III-600Y/72.5B-10193W |  | III | 600 | Y | 72.5 | B | 10193W | 1 | 28 | 34.5 | 468.6 | 520.6 | 249 |  | 8 |  |  | SHM-D | ok | type_from_oltc_data
E-CM2260258 意大利TAMINI.pdf | VCM | E-CM2260258 | 意大利TAMINI | CM2 | [8 empty] | 1 | 51.72 | 150 | 199.1 | 227.5 | 1875 |  |  |  |  | CMA7 | ok | no_type
E-CM2260259 土耳其HMT-BETA.pdf | VCM | E-CM2260259 | 土耳其HMT-BETA | CM2 | CM2III-500Y/72.5C-10191G |  | III | 500 | Y | 72.5 | C | 10191G | 1 | 70 | 115 | 351.4 | 418.38 | 1180.5 |  | 9 |  |  | CMA7 | ok | type_from_oltc_data
E-CM2260260-261 土耳其HMT-Elsewedy.pdf | VCM | E-CM2260260-261 | 土耳其HMT-Elsewedy | CM2 | CM2III-500Y/170C-10193W |  | III | 500 | Y | 170 | C | 10193W | 2 | 80 | 220 | 209.9 | 233.3 | 1587.7 |  | 8 |  |  | CMA7 | ok | type_from_oltc_data
E-CM2260262 意大利GBE.pdf | VCM | E-CM2260262 | 意大利GBE | CM2 | CM2III-500Y/126B-10191W |  | III | 500 | Y | 126 | B | 10191W | 1 | 63 | 115 | 316.29 |  | 1183 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CM2260263 印尼BAMBANGDJAJA.pdf | VCM | E-CM2260263 | 印尼BAMBANGDJAJA | CM2 | [9 empty] | 28 | 115 | 140.57 | 156.19 | 414.97 |  | 16 | 16 | 16 | CMA7 | ok | no_type
E-CM2260263 印尼BAMBANGDJAJA0730.pdf | VCM | E-CM2260263 | 印尼BAMBANGDJAJA0730 | CM2 | [9 empty] | 28 | 115 | 140.57 | 156.19 | 414.97 |  | 16 | 16 | 16 | CMA7 | ok | no_type
E-CM2260264-265 意大利TAMINI.pdf | VCM | E-CM2260264-265 | 意大利TAMINI | CM2 | CM2III-500Y/170B-12233W | CM2III-600Y/170B-12233W | III | 500 | Y | 170 | B | 12233W | 1 | 0.11 | 150 | 423.4 | 483.9 | 1082.5 |  |  |  |  | CMA7 | ok | page_timeout_at_12; type_from_oltc_data
E-CM2260266 澳大利亚HUB ELECTRIC 售后.pdf | VCM | E-CM2260266 | 澳大利亚HUB ELECTRIC 售后 | CM2 | [19 empty] | scanned_or_empty
E-CM2260267 美国HMUS-C.E.M..pdf | VCM | E-CM2260267 | 美国HMUS-C.E.M. | CM2 | 3xCM2I-1500/72.5B-18180 | CM2I-1500/72.5B-18180 ¦ WSLIV-1600D/72.5-7x6D ¦ WSLIV-1600D/72.5-7x6 | I | 1500 |  | 72.5 | B | 18180 | 3 | 50.4 | 13.8 |  |  |  | 798 |  |  |  | CMA7 | ok | type_from_oltc_data
E-CM2260268-270 巴西COMTRAFO.pdf | VCM | E-CM2260268-270 | 巴西COMTRAFO | CM2 | CM2III-600Y/72.5B-12233W | CM2III-600Y/72.5C-12233W | III | 600 | Y | 72.5 | B | 12233W | 3 | 150 | 230 | 376.5 |  | 1328 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CM2260271-272 土耳其HMT-BEST.pdf | VCM | E-CM2260271-272 | 土耳其HMT-BEST | CM2 | CM2III-500Y/252D-16313G |  | III | 500 | Y | 252 | D | 16313G | 2 | 100 | 159 | 363.1 | 403.5 | 917.9 |  |  | 18 | 10 |  | ok | type_from_oltc_data
E-CM2260273 俄罗斯HMR-JSHC.pdf | VCM | E-CM2260273 | 俄罗斯HMR-JSHC | CM2 | 3xCM2I-1200/170C-14131W |  | I | 1200 |  | 170 | C | 14131W | 3 | 199 | 330 | 1000 | 1063 | 1328 |  | 6 |  |  | CMA7 | ok | type_from_oltc_data
E-CM2260274-277 土耳其HMT-ZTR.pdf | VCM | E-CM2260274-277 | 土耳其HMT-ZTR | CM2 | 3xCM2I-1200/170C-14130 | 3xCM2I-800/170C-14130 | I | 1200 |  | 170 | C | 14130 | 3 | 200 | [9 empty] | ok | po_not_os; type_from_compact
E-CM2260278 土耳其HMT-ZTR.pdf | VCM | E-CM2260278 | 土耳其HMT-ZTR | CM2 | 3xCM2I-1200/170C-14130 | 3xCM2I-800/170C-14130 | I | 1200 |  | 170 | C | 14130 | 3 | 200 | [9 empty] | ok | po_not_os; type_from_compact
E-CM2260279 秘鲁Delcrosa.pdf | VCM | E-CM2260279 | 秘鲁Delcrosa | CM2 | CM2III-500Y/72.5B-14271W |  | III | 500 | Y | 72.5 | B | 14271W | 1 | 7.5 | 66 | 65.61 |  | 381.05 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CM2260280-281 俄罗斯HMR-SIEMENS.pdf | VCM | E-CM2260280-281 | 俄罗斯HMR-SIEMENS | CM2 | CM2III-500Y/72.5C-14273W |  | III | 500 | Y | 72.5 | C | 14273W | 1 | 63 | 230 | 158 | 167 | 1328 |  | 12 |  |  | CMA7 | ok | type_from_oltc_data
E-CM2260282-283 俄罗斯HMR-SIEMENS.pdf | VCM | E-CM2260282-283 | 俄罗斯HMR-SIEMENS | CM2 | CM2III-500Y/72.5B-14273W |  | III | 500 | Y | 72.5 | B | 14273W | 1 | 63 | 230 | 158 | 167 | 1328 |  | 12 |  |  | CMA7 | ok | type_from_oltc_data
E-CM2260284 缅甸PTE.pdf | VCM | E-CM2260284 | 缅甸PTE | CM2 | CM2III-500Y/170D-14273G |  | III | 500 | Y | 170 | D | 14273G | 1 | 100 | 230 | 251 | 313.78 | 1660 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CM2260285 印尼HMPI 型式试验.pdf | VCM | E-CM2260285 | 印尼HMPI 型式试验 | CM2 | [19 empty] | scanned_or_empty
E-CV2260001-004 巴西WEG.pdf | VCV | E-CV2260001-004 | 巴西WEG | CV2 | CV2III-350D/145-10193W |  | III | 350 | D | 145 |  | 10193W | 4 | 26.6 | 138 | 64.26 |  | 1725 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260005-006 巴西WEG.pdf | VCV | E-CV2260005-006 | 巴西WEG | CV2 | CV2III-350D/145-10193W |  | III | 350 | D | 145 |  | 10193W | 2 | 26.6 | 138 | 64.25 |  | 1725 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260007 巴西WEG.pdf | VCV | E-CV2260007 | 巴西WEG | CV2 | CV2III-350D/72.5-10193W |  | III | 350 | D | 72.5 |  | 10193W | 1 | 26.6 | 69 | 128.5 |  | 862.5 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260008-009 巴西WEG.pdf | VCV | E-CV2260008-009 | 巴西WEG | CV2 | CV2III-350Y/72.5-10193W |  | III | 350 | Y | 72.5 |  | 10193W | 2 | 20 | 69 | 167.3 |  | 747 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260010-014 巴西WEG.pdf | VCV | E-CV2260010-014 | 巴西WEG | CV2 | CV2III-350D/72.5-10193W |  | III | 350 | D | 72.5 |  | 10193W | 5 | 20 | 69 | 96.6 |  | 862.5 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260015 巴西WEG.pdf | VCV | E-CV2260015 | 巴西WEG | CV2 | CV2III-350Y/72.5-10193W |  | III | 350 | Y | 72.5 |  | 10193W | 1 | 26.6 | 138 | 111.3 |  | 995.9 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260016 巴西WEG.pdf | VCV | E-CV2260016 | 巴西WEG | CV2 | CV2III-350D/40.5-10193W |  | III | 350 | D | 40.5 |  | 10193W | 1 | 12.5 | 34.5 | 120.8 |  | 431.25 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260017 巴西WEG.pdf | VCV | E-CV2260017 | 巴西WEG | CV2 | CV2III-600Y/40.5-10193W |  | III | 600 | Y | 40.5 |  | 10193W | 1 | 40 | 72.45 | 334.7 |  | 862.5 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260018 巴西WEG.pdf | VCV | E-CV2260018 | 巴西WEG | CV2 | CV2III-350D/145-10193W |  | III | 350 | D | 145 |  | 10193W | 1 | 12.5 | 138 | 30.2 |  | 1725 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260019 巴西WEG.pdf | VCV | E-CV2260019 | 巴西WEG | CV2 | CV2III-350Y/72.5-10193W |  | III | 350 | Y | 72.5 |  | 10193W | 1 | 26.6 | 69 | 222.6 |  | 497.68 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260020 缅甸 Power Tagun Engineering.pdf | VCV | E-CV2260020 | 缅甸 Power Tagun Engineering | CV2 | CV2III-350D/72.5-10193W |  | III | 350 | D | 72.5 |  | 10193W | 1 | 30 | 66 | 151.5 | 181.5 | 1089 |  |  |  |  | SHM-K, CMA7, SHM-D | ok | type_from_oltc_data
E-CV2260021 缅甸 Power Tagun Engineering.pdf | VCV | E-CV2260021 | 缅甸 Power Tagun Engineering | CV2 | CV2III-350Y/72.5-10193W |  | III | 350 | Y | 72.5 |  | 10193W | 1 | [9 empty] | CMA7 | ok | po_not_os; type_from_compact
E-CV2260022-023 意大利ALTRAFO.pdf | VCV | E-CV2260022-023 | 意大利ALTRAFO | CV2 | CV2III-350D/40.5-12231W |  | III | 350 | D | 40.5 |  | 12231W | 2 | 11 | 30 | 122 |  | 450 |  |  |  |  | CMA7 | ok | type_from_compact
E-CV2260024 俄罗斯HMR-SVEL.pdf | VCV | E-CV2260024 | 俄罗斯HMR-SVEL | CV2 | CV2III-600D/145-10193W |  | III | 600 | D | 145 |  | 10193W | 1 | 63 | 121 | 301 | 342 | 1048 |  | 8 |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260025-029 土耳其HMT-TASKIN Consultancy.pdf | VCV | E-CV2260025-029 | 土耳其HMT-TASKIN Consultancy | CV2 | CV2III-600Y/72.5-10191W |  | III | 600 | Y | 72.5 |  | 10191W | 5 | 50 | [9 empty] | ok | po_not_os; type_from_compact
E-CV2260030 巴西WEG.pdf | VCV | E-CV2260030 | 巴西WEG | CV2 | CV2III-350Y/72.5-12233W |  | III | 350 | Y | 72.5 |  | 12233W | 1 | 25 | 138 | 104.6 |  | 797 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260031-037 巴西WEG.pdf | VCV | E-CV2260031-037 | 巴西WEG | CV2 | CV2III-350D/145-10193W |  | III | 350 | D | 145 |  | 10193W | 7 | [10 empty] | ok | po_not_os; type_from_compact
E-CV2260038-039 缅甸 Power Tagun Engineering.pdf | VCV | E-CV2260038-039 | 缅甸 Power Tagun Engineering | CV2 | CV2III-350D/72.5-10193W |  | III | 350 | D | 72.5 |  | 10193W | 2 | [9 empty] | SHM-K | ok | po_not_os; type_from_compact
E-CV2260040 巴西WEG.pdf | VCV | E-CV2260040 | 巴西WEG | CV2 | CV2III-350Y/72.5-12231W |  | III | 350 | Y | 72.5 |  | 12231W | 1 | [10 empty] | ok | po_not_os; type_from_compact
E-CV2260041-043 巴西WEG.pdf | VCV | E-CV2260041-043 | 巴西WEG | CV2 | CV2III-350D/72.5-10193W |  | III | 350 | D | 72.5 |  | 10193W | 3 | [9 empty] | CMA7 | ok | page_timeout_at_12; po_not_os; type_from_compact
E-CV2260044-045 巴西WEG.pdf | VCV | E-CV2260044-045 | 巴西WEG | CV2 | CV2III-350D/145-10193W |  | III | 350 | D | 145 |  | 10193W | 2 | [9 empty] | CMA7 | ok | page_timeout_at_12; po_not_os; type_from_compact
E-CV2260046 巴西WEG.pdf | VCV | E-CV2260046 | 巴西WEG | CV2 | CV2III-350D/145-10193W |  | III | 350 | D | 145 |  | 10193W | 1 | [10 empty] | ok | po_not_os; type_from_compact
E-CV2260047 印尼 GE UNINDO.pdf | VCV | E-CV2260047 | 印尼 GE UNINDO | CV2 | CV2III-350Y/72.5-10193G | CV2III-350Y/72.5-10191G | III | 350 | Y | 72.5 |  | 10193G | 1 | 60 | 150 | 230.9 | 256.6 |  |  | 8 |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260048-049 巴西WEG.pdf | VCV | E-CV2260048-049 | 巴西WEG | CV2 | CV2III-350Y/72.5-10193W |  | III | 350 | Y | 72.5 |  | 10193W | 2 | 26.6 | 69 | 222.57 |  | 498 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260050 印尼GE.pdf | VCV | E-CV2260050 | 印尼GE | CV2 | CV2III-350Y/72.5-10193G | CV2III-350Y/72.5-10191G | III | 350 | Y | 72.5 |  | 10193G | 1 | 30 | 150 | 115.5 | 128.3 |  |  |  | 8 | 8 | CMA7 | ok | type_from_oltc_data
E-CV2260051-052 缅甸 PTE.pdf | VCV | E-CV2260051-052 | 缅甸 PTE | CV2 | CV2III-350Y/72.5-10193W |  | III | 350 | Y | 72.5 |  | 10193W | 2 | [9 empty] | CMA7 | ok | po_not_os; type_from_compact
E-CV2260053-054 俄罗斯HMR-TOGLIATTI.pdf | VCV | E-CV2260053-054 | 俄罗斯HMR-TOGLIATTI | CV2 | CV2III-350Y/72.5-10191W |  | III | 350 | Y | 72.5 |  | 10191W | 2 | 40 | 115 | 200.8 | 212.1 | 1182 |  | 9 |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260055-056 越南EEMC.pdf | VCV | E-CV2260055-056 | 越南EEMC | CV2 | CV2III-600Y/72.5-10191W |  | III | 600 | Y | 72.5 |  | 10191W | 2 | [9 empty] | CMA7 | ok | po_not_os; type_from_compact
E-CV2260057 印度TOSHIBA.pdf | VCV | E-CV2260057 | 印度TOSHIBA | CV2 | CV2III-600Y/72.5-1 | 2xSHZVIII-400Y/170D-3 ¦ SHZVIII-400Y/170D-2 | III | 600 | Y | 72.5 |  | 1 | 1 | 55 | [8 empty] | CMA7 | ok | po_not_os; type_from_compact
E-CV2260058 秘鲁Delcrosa.pdf | VCV | E-CV2260058 | 秘鲁Delcrosa | CV2 | CV2III-350Y/72.5-12233W |  | III | 350 | Y | 72.5 | B | 12233W | 1 | 15 | 63 | 138 |  | 363.7 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260059-060 土耳其HMT-Green Transfo.pdf | VCV | E-CV2260059-060 | 土耳其HMT-Green Transfo | CV2 | CV2III-600D/40.5-10193G |  | III | 600 | D | 40.5 |  | 10193G | 2 | 37 | 33 | 373.7 | 415.3 | 412.5 |  | 8 |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260061 土耳其HMT-ZTR.pdf | VCV | E-CV2260061 | 土耳其HMT-ZTR | CV2 | CV2III-350Y/72.5-10191W |  | III | 350 | Y | 72.5 |  | 10191W | 1 | 40 | [8 empty] | HMC-3C | ok | po_not_os; type_from_compact
E-CV2260062-064 土耳其HMT-ZTR.pdf | VCV | E-CV2260062-064 | 土耳其HMT-ZTR | CV2 | CV2III-350Y/126-10193W |  | III | 350 | Y | 126 |  | 10193W | 3 | 80 | [8 empty] | HMC-3C | ok | po_not_os; type_from_compact
E-CV2260065-066 巴西WEG.pdf | VCV | E-CV2260065-066 | 巴西WEG | CV2 | CV2III-350D/145-10193W | CV2III-250D/145-10193W | III | 350 | D | 145 |  | 10193W | 2 | 12.5 | 138 | 30.2 |  | 1725 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260067 巴西WEG.pdf | VCV | E-CV2260067 | 巴西WEG | CV2 | CV2III-350Y/72.5-10193W |  | III | 350 | Y | 72.5 |  | 10193W | 2 | 50 | 138 | 209.18 |  | 996 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260068-069 巴西WEG.pdf | VCV | E-CV2260068-069 | 巴西WEG | CV2 | CV2III-350D/145-10193W |  | III | 350 | D | 145 |  | 10193W | 2 | 40 | 138 | 96.6 |  | 1725 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260070-071 俄罗斯.pdf | VCV | E-CV2260070-071 | 俄罗斯 | CV2 | [8 empty] | 2 | [10 empty] | ok | page_timeout_at_7; no_type
E-CV2260072 俄罗斯HMR-SIEMENS.pdf | VCV | E-CV2260072 | 俄罗斯HMR-SIEMENS | CV2 | CV2III-600D/40.5-10193W |  | III | 600 | D | 40.5 |  | 10193W | 1 | 25 | 15.75 | 529 | 563 | 236.3 |  | 8 |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260073 巴西WEG.pdf | VCV | E-CV2260073 | 巴西WEG | CV2 | CV2III-350D/145-10193W |  | III | 350 | D | 145 |  | 10193W | 1 | 20 | 138 | 48.3 |  | 1725 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260074 巴西WEG.pdf | VCV | E-CV2260074 | 巴西WEG | CV2 | CV2III-350D/72.5-10193W |  | III | 350 | D | 72.5 |  | 10193W | 1 | 12.5 | 69 | 60.37 |  | 862.5 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260075-076 巴西WEG.pdf | VCV | E-CV2260075-076 | 巴西WEG | CV2 | CV2III-350D/72.5-10193W |  | III | 350 | D | 72.5 |  | 10193W | 2 | 12.5 | 69 | 60.37 |  | 862.5 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260077 巴西TRAEL.pdf | VCV | E-CV2260077 | 巴西TRAEL | CV2 | CV2III-350Y/40.5-10193W |  | III | 350 | Y | 40.5 |  | 10193W | 1 | 30 | 69 | 251 | 278.9 | 862.5 |  | 8 |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260078 南非Radian TRC.pdf | VCV | E-CV2260078 | 南非Radian TRC | CV2 | CV2III-350D/40.5-10070 |  | III | 350 | D | 40.5 |  | 10070 | 1 | 2.452 | 6.6 | 215 | 215 |  | 911.1 |  |  | 17 | CMA7 | ok | type_from_compact
E-CV2260079-082 土耳其HMT-MEKSAN.pdf | VCV | E-CV2260079-082 | 土耳其HMT-MEKSAN | CV2 | CV2III-350D/40.5-10193G |  | III | 350 | D | 40.5 |  | 10193G | 4 | 6.5 | 33 | 65.7 | 75.8 | 551 |  | 8 |  |  | ET-SZ6, CMA7 | ok | type_from_oltc_data
E-CV2260083-085 巴西WEG.pdf | VCV | E-CV2260083-085 | 巴西WEG | CV2 | CV2III-350D/72.5-10193W |  | III | 350 | D | 72.5 |  | 10193W | 3 | [10 empty] | ok | page_timeout_at_12; po_not_os; type_from_compact
E-CV2260086-087 巴西WEG.pdf | VCV | E-CV2260086-087 | 巴西WEG | CV2 | CV2III-350Y/40.5-10193W |  | III | 350 | Y | 40.5 |  | 10193W | 2 | 12.5 | 34.5 | 209.18 |  | 431.25 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260088 南非ACTOM.pdf | VCV | E-CV2260088 | 南非ACTOM | CV2 | [8 empty] | 2 | 40 | 66 | 202 | 238 | 825 |  |  |  |  | CMA7 | ok | no_type
E-CV2260089-095 哈萨克斯坦 ASIA TRAFO.pdf | VCV | E-CV2260089-095 | 哈萨克斯坦 ASIA TRAFO | CV2 | [8 empty] | 7 | 35 | 110 |  |  | 1958 |  | 9 |  |  | CMA7 | ok | no_type
E-CV2260096-098 南非Raiju.pdf | VCV | E-CV2260096-098 | 南非Raiju | CV2 | CV2III-600D/40.5-10193G |  | III | 600 | D | 40.5 |  | 10193G | 1 | 30 | 33 | 303 | 356 | 410 |  |  | 4 | 12 | CMA7 | ok | type_from_oltc_data
E-CV2260099 巴西TRAEL.pdf | VCV | E-CV2260099 | 巴西TRAEL | CV2 | CV2III-350D/145-10193W | CV2III-350D/72.5-10193W | III | 350 | D | 145 |  | 10193W | 1 | 30 | 138 | 72.5 | 80.5 | 1725 |  | 8 |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260100 俄罗斯HMR-SVEL.pdf | VCV | E-CV2260100 | 俄罗斯HMR-SVEL | CV2 | CV2III-350Y/72.5-10191W |  | III | 350 | Y | 72.5 |  | 10191W | 1 | 40 | 115 | 201 | 212 | 1184 |  | 9 |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260101-103 土耳其HMT-Taskin Colsultancy.pdf | VCV | E-CV2260101-103 | 土耳其HMT-Taskin Colsultancy | CV2 | CV2III-600D/40.5-10193G |  | III | 600 | D | 40.5 |  | 10193G | 3 | 40 | 33 | 404.1 | 442.8 | 412.5 |  | 7 |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260104 俄罗斯HMR-SVEL.pdf | VCV | E-CV2260104 | 俄罗斯HMR-SVEL | CV2 | CV2III-350Y/72.5-10191W |  | III | 350 | Y | 72.5 |  | 10191W | 1 | 63 | 115 | 316 | 334 | 1184 |  | 9 |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260105-106 巴西TRAEL 以此为准.pdf | VCV | E-CV2260105-106 | 巴西TRAEL 以此为准 | CV2 | CV2III-350D/145-12231W | CV2III-350D/72.5-10193W ¦ CV2III-600Y/72.5-10193W ¦ CV2III-350D/145-10193W | III | 350 | D | 145 |  | 12231W | 2 | 20 | 84 | 79.4 | 88.2 | 763.6 |  | 11 |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260105-106 巴西TRAEL.pdf | VCV | E-CV2260105-106 | 巴西TRAEL | CV2 | CV2III-350D/145-12231W | CV2III-350D/72.5-10193W ¦ CV2III-600Y/72.5-10193W ¦ CV2III-350D/145-10193W | III | 350 | D | 145 |  | 12231W | 2 | 41.5 | 138 | 79.4 | 88.2 | 763.5 |  | 11 |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260107 巴西TRAEL.pdf | VCV | E-CV2260107 | 巴西TRAEL | CV2 | CV2III-350D/72.5-10193W | CV2III-350D/145-10193W | III | 350 | D | 72.5 |  | 10193W | 1 | 25 | 69 | 120.77 | 142.3 | 862.5 |  |  | 4 | 12 | CMA7 | ok | type_from_oltc_data
E-CV2260108 巴西TRAEL.pdf | VCV | E-CV2260108 | 巴西TRAEL | CV2 | CV2III-350D/145-10193W | CV2III-350D/72.5-10193W | III | 350 | D | 145 |  | 10193W | 1 |  |  | 36.2 | 40.3 | [5 empty] | CMA7 | ok | type_from_oltc_data
E-CV2260109 巴西TRAEL.pdf | VCV | E-CV2260109 | 巴西TRAEL | CV2 | CV2III-350D/145-10193W | CV2III-350D/72.5-10193W | III | 350 | D | 145 |  | 10193W | 1 | 30 | 138 | 72.5 | 80.5 | 1725 |  | 8 |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260110 印尼GE.pdf | VCV | E-CV2260110 | 印尼GE | CV2 | CVIII-350Y/72.5-10193W | CV2III-350Y/72.5-10193W ¦ CV2III-350Y/72.51-0193W | III | 350 | Y | 72.5 |  | 10193W | 1 | 50 | 150 | 192.5 | 213.8 |  |  |  | 8 | 8 | CMA7 | ok | type_from_oltc_data
E-CV2260111 俄罗斯HMR-JSHC.pdf | VCV | E-CV2260111 | 俄罗斯HMR-JSHC | CV2 | CV2III-350Y/72.5-10191W |  | III | 350 | Y | 72.5 |  | 10191W | 1 | 40 | 115 | 201 | 212 | 1182 |  | 9 |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260112 巴西WEG.pdf | VCV | E-CV2260112 | 巴西WEG | CV2 | CV2III-600D/126-10193W |  | III | 600 | D | 126 |  | 10193W | 2 | 41.66 | 138 | 348.6 |  | 497.96 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260113-114 巴西WEG.pdf | VCV | E-CV2260113-114 | 巴西WEG | CV2 | CV2III-350D/72.5-10193W |  | III | 350 | D | 72.5 |  | 10193W | 2 | 20 | 69 | 96.6 |  | 862.5 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260115 哥伦比亚WEG.pdf | VCV | E-CV2260115 | 哥伦比亚WEG | CV2 | CV2III-350D/72.5-10193W | CV2III-350D/72.5-10193 | III | 350 | D | 72.5 |  | 10193W | 2 | 12 | 44 | 90.9 |  | 550 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260116-117 巴西DATA.pdf | VCV | E-CV2260116-117 | 巴西DATA | CV2 | CV2III-350D/145-12233W |  | III | 350 | D | 145 |  | 12233W | 2 | 0.04 | 138 | 96.6 |  | 1725 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260118-119 俄罗斯HMR-SIEMENS.pdf | VCV | E-CV2260118-119 | 俄罗斯HMR-SIEMENS | CV2 | CV2III-600D/40.5-10193W |  | III | 600 | D | 40.5 |  | 10193W | 1 | 25 | 15.75 | 529 | 563 | 236.3 |  |  |  |  | CMA7 | ok | page_timeout_at_11; type_from_oltc_data
E-CV2260120 巴西WEG.pdf | VCV | E-CV2260120 | 巴西WEG | CV2 | CV2III-350Y/72.5-10193W |  | III | 350 | Y | 72.5 |  | 10193W | 1 | 40 | 138 | 167.3 |  | 996 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260121 巴西WEG.pdf | VCV | E-CV2260121 | 巴西WEG | CV2 | CV2III-350D/145-10193W | CV2III-250D/145-10193W | III | 350 | D | 145 |  | 10193W | 1 | 12.5 | 138 | 30.2 |  | 1725 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260122 巴西WEG.pdf | VCV | E-CV2260122 | 巴西WEG | CV2 | CV2III-350Y/72.5-10193W |  | III | 350 | Y | 72.5 |  | 10193W | 1 | 50 | 138 | 220.2 |  | 995.9 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260123-124 巴西WEG.pdf | VCV | E-CV2260123-124 | 巴西WEG | CV2 | CV2III-350D/145-10193W |  | III | 350 | D | 145 |  | 10193W | 2 | 33.3 | 138 | 80.44 |  | 1725 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260125 巴西TRAEL.pdf | VCV | E-CV2260125 | 巴西TRAEL | CV2 | CV2III-350D/145-10193W | CV2III-350D/72.5-10193W | III | 350 | D | 145 |  | 10193W | 1 | 20 | 138 | 48.32 | 56.81 | 1725 |  |  | 4 | 12 | CMA7 | ok | type_from_oltc_data
E-CV2260126 巴西WEG.pdf | VCV | E-CV2260126 | 巴西WEG | CV2 | CV2III-350Y/40.5-10193W |  | III | 350 | Y | 40.5 |  | 10193W | 1 | 15 | 69 | 125.5 |  | 497.96 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260127-129 土耳其HMT-Beta Transformer.pdf | VCV | E-CV2260127-129 | 土耳其HMT-Beta Transformer | CV2 | CV2III-600Y/72.5-10191W |  | III | 600 | Y | 72.5 |  | 10191W | 3 | 62 | 121 | 295.8 | 352.2 | 1242.1 |  | 9 |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260130 巴西WEG.pdf | VCV | E-CV2260130 | 巴西WEG | CV2 | CV2III-350D/145-10193W |  | III | 350 | D | 145 |  | 10193W | 1 | 19.5 | 151.8 | 47.1 |  | 1725 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260131-132 缅甸PTE.pdf | VCV | E-CV2260131-132 | 缅甸PTE | CV2 | [8 empty] | 2 | [9 empty] | CMA7 | ok | po_not_os; no_type
E-CV2260133巴西WEG.pdf | VCV | E-CV2260133 | 巴西WEG | CV2 | CV2III-350Y/72.5-10193W |  | III | 350 | Y | 72.5 |  | 10193W | 1 | 50 | 138 | 209.2 |  | 996 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260134-135 缅甸PTE.pdf | VCV | E-CV2260134-135 | 缅甸PTE | CV2 | [8 empty] | 2 | [9 empty] | CMA7 | ok | po_not_os; no_type
E-CV2260136 巴西WEG.pdf | VCV | E-CV2260136 | 巴西WEG | CV2 | CV2III-350Y/72.5-10193W |  | III | 350 | Y | 72.5 |  | 10193W | 1 | 50 | 138 | 209.2 |  | 996 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260137 巴西WEG.pdf | VCV | E-CV2260137 | 巴西WEG | CV2 | CV2III-350Y/40.5-10193W |  | III | 350 | Y | 40.5 |  | 10193W | 1 | 6.25 | 34.5 | 104.6 |  | 431.25 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260139-145 土耳其HMT-Nexans Maroc.pdf | VCV | E-CV2260139-145 | 土耳其HMT-Nexans Maroc | CV2 | CV2III-600Y/72.5-12233G |  | III | 600 | Y | 72.5 |  | 12233G | 7 | 40 | 63 | 367 |  | 545 |  | 10 |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260146-147 俄罗斯HMR-SIEMENS.pdf | VCV | E-CV2260146-147 | 俄罗斯HMR-SIEMENS | CV2 | CV2III-350Y/72.5-10191W |  | III | 350 | Y | 72.5 |  | 10191W | 1 | 63 | 115 | 316.3 | 334.1 | 1182 |  |  |  |  | CMA7 | ok | page_timeout_at_12; type_from_oltc_data
E-CV2260148 巴西TRAEL.pdf | VCV | E-CV2260148 | 巴西TRAEL | CV2 | CV2III-350D/145-10193W | CV2III-350D/72.5-10193W ¦ CV2III-350D/145-10193 | III | 350 | D | 145 |  | 10193W | 1 | 20 | 138 | 48.32 | 56.8 | 1725 |  |  | 4 | 12 | CMA7 | ok | type_from_oltc_data
E-CV2260149-150 巴西TRAEL.pdf | VCV | E-CV2260149-150 | 巴西TRAEL | CV2 | CV2III-350D/145-10193W | CV2III-350D/72.5-10193W | III | 350 | D | 145 |  | 10193W | 2 | 40 | 138 | 96.59 | 113.68 | 1725 |  |  | 4 | 12 | CMA7 | ok | type_from_oltc_data
E-CV2260151 巴西TRAEL.pdf | VCV | E-CV2260151 | 巴西TRAEL | CV2 | CV2III-350D/72.5-10193W | CV2III-350D/145-10193W | III | 350 | D | 72.5 |  | 10193W | 1 | 12.5 | 69 | 60.39 | 71.01 | 862.5 |  |  | 4 | 12 | CMA7 | ok | type_from_oltc_data
E-CV2260152-155 巴西TRAEL.pdf | VCV | E-CV2260152-155 | 巴西TRAEL | CV2 | CV2III-350D/72.5-10193W | CV2III-350D/145-10193W | III | 350 | D | 72.5 |  | 10193W | 4 | 12.5 | 69 | 60.39 | 71.01 | 862.5 |  |  | 4 | 12 | CMA7 | ok | type_from_oltc_data
E-CV2260156 巴西TRAEL.pdf | VCV | E-CV2260156 | 巴西TRAEL | CV2 | CV2III-350D/72.5-10193W | CV2III-350D/145-10193W | III | 350 | D | 72.5 |  | 10193W | 1 | 12.5 | 69 | 60.39 | 71.01 | 862.5 |  |  | 4 | 12 | CMA7 | ok | type_from_oltc_data
E-CV2260157-159 捷克Revos-ZREW.pdf | VCV | E-CV2260157-159 | 捷克Revos-ZREW | CV2 | CV2III-600Y/72.5-10193G |  | III | 600 | Y | 72.5 |  | 10193G | 1 | 63 | 110 | 330.7 | 393.6 | 1270.2 |  | 8 |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260160-161 哈萨克斯坦 ASIA TRAFO.pdf | VCV | E-CV2260160-161 | 哈萨克斯坦 ASIA TRAFO | CV2 | [8 empty] | 2 | 50 | 110 |  |  | 1958 |  | 9 |  |  | CMA7 | ok | no_type
E-CV2260162-164 捷克Revos-Koncar.pdf | VCV | E-CV2260162-164 | 捷克Revos-Koncar | CV2 | CV2III-600Y/72.5-10193G |  | III | 600 | Y | 72.5 |  | 10193G | 3 | [9 empty] | CMA7 | ok | type_from_compact
E-CV2260165-166 俄罗斯HMR-SIEMENS 售后.pdf | VCV | E-CV2260165-166 | 俄罗斯HMR-SIEMENS 售后 | CV2 | CV2III-600Y/72.5-10191W |  | III | 600 | Y | 72.5 |  | 10191W | 1 | 63 | 115 | 332.1 | 351 | 1182 |  | 9 |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260167-169 巴西WEG.pdf | VCV | E-CV2260167-169 | 巴西WEG | CV2 | CV2III-350D/72.5-10193W |  | III | 350 | D | 72.5 |  | 10193W | 3 | 33.3 | 69 | 160.9 |  | 862.5 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260170 巴西COMTRAFO.pdf | VCV | E-CV2260170 | 巴西COMTRAFO | CV2 | CV2III-350D/145-10193W |  | III | 350 | D | 145 |  | 10193W | 1 | 25 | 138 |  |  | 1725 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260171 土耳其HMT-TASKIN Consultancy.pdf | VCV | E-CV2260171 | 土耳其HMT-TASKIN Consultancy | CV2 | CV2III-600Y/72.5-10191W |  | III | 600 | Y | 72.5 |  | 10191W | 1 | 40 | 63 | 367 | 432 | 606 |  | 9 |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260172 泰国TIRATHAI.pdf | VCV | E-CV2260172 | 泰国TIRATHAI | CV2 | [19 empty] | scanned_or_empty | page_err_12:PdfminerException
E-CV2260173 南非 Raiju.pdf | VCV | E-CV2260173 | 南非 Raiju | CV2 | CV2III-350Y/72.5-10193W |  | III | 350 | Y | 72.5 |  | 10193W | 1 | 30 | 66 | 174.95 | 205.83 | 476 |  |  | 4 | 12 |  | ok | type_from_compact
E-CV2260174-176 巴西TRAEL.pdf | VCV | E-CV2260174-176 | 巴西TRAEL | CV2 | CV2III-350D/72.5-10193W |  | III | 350 | D | 72.5 |  | 10193W | 3 | 12.5 | 69 | 60.39 | 71.01 | 862.5 |  |  | 4 | 12 | CMA7 | ok | type_from_oltc_data
E-CV2260177-178 巴西TRAEL.pdf | VCV | E-CV2260177-178 | 巴西TRAEL | CV2 | CV2III-350D/72.5-10193W | CV2III-600Y/72.5-10193W ¦ CV2III-350D/72.5-10193 ¦ CV2III-350D/145-12231W ¦ CV2III-350D/145-10193W | III | 350 | D | 72.5 |  | 10193W | 2 | 12.5 | 69 | 59.6 | 71 | 862.5 |  |  | 4 | 12 | CMA7 | ok | type_from_oltc_data
E-CV2260179-180 巴西TRAEL.pdf | VCV | E-CV2260179-180 | 巴西TRAEL | CV2 | CV2III-350D/72.5-10193W | CV2III-600Y/72.5-10193W ¦ CV2III-350D/145-12231W ¦ CV2III-350D/145-10193W | III | 350 | D | 72.5 |  | 10193W | 2 | 50 | 69 | 241.5 | 268.3 | 862.5 |  | 8 |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260181-182 巴西TRAEL.pdf | VCV | E-CV2260181-182 | 巴西TRAEL | CV2 | CV2III-350D/145-10193W | CV2III-350D/72.5-10193W ¦ CV2III-600Y/72.5-10193W ¦ CV2III-350D/145-12231W | III | 350 | D | 145 |  | 10193W | 2 | 60 | 138 | 144.9 | 161 | 1725 |  | 8 |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260183-184 巴西TRAEL.pdf | VCV | E-CV2260183-184 | 巴西TRAEL | CV2 | CV2III-600Y/72.5-10193W | CV2III-350D/72.5-10193W ¦ CV2III-350D/145-12231W ¦ CV2III-350D/145-10193W | III | 600 | Y | 72.5 |  | 10193W | 2 | 50 | 69 | 418.4 | 464.9 | 862.5 |  | 8 |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260185 巴西TRAEL.pdf | VCV | E-CV2260185 | 巴西TRAEL | CV2 | CV2III-350D/145-10193W | CV2III-350D/72.5-10193W | III | 350 | D | 145 |  | 10193W | 1 | 30 | 138 | 72.5 | 85.3 | 1725 |  |  | 4 | 12 | CMA7 | ok | type_from_oltc_data
E-CV2260186-187 巴西TRAEL.pdf | VCV | E-CV2260186-187 | 巴西TRAEL | CV2 | CV2III-350D/145-10193W | CV2III-350D/72.5-10193W | III | 350 | D | 145 |  | 10193W | 2 | 15 | 138 | 36.2 | 42.6 | 1725 |  |  | 4 | 12 | CMA7 | ok | type_from_oltc_data
E-CV2260188 巴西TRAEL.pdf | VCV | E-CV2260188 | 巴西TRAEL | CV2 | CV2III-350D/145-10193W | CV2III-350D/72.5-10193W | III | 350 | D | 145 |  | 10193W | 1 | 15 | 138 | 36.3 | 40.3 | 1725 |  | 8 |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260189-190 巴西TRAEL.pdf | VCV | E-CV2260189-190 | 巴西TRAEL | CV2 | CV2III-350D/72.5-10193W | CV2III-350D/72.5-10193 ¦ CV2III-350D/145-10193W | III | 350 | D | 72.5 |  | 10193W | 2 | 15 | 69 | 72.46 | 80.51 | 862.5 |  | 8 |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260191-193 巴西TRAEL.pdf | VCV | E-CV2260191-193 | 巴西TRAEL | CV2 | CV2III-350D/72.5-10193W | CV2III-350D/145-10193W | III | 350 | D | 72.5 |  | 10193W | 3 | 12.5 | 69 | 60.39 | 71.01 | 862.5 |  |  | 4 | 12 | CMA7 | ok | type_from_oltc_data
E-CV2260194 巴西TRAEL.pdf | VCV | E-CV2260194 | 巴西TRAEL | CV2 | CV2III-350D/72.5-10193W | CV2III-350D/145-10193W | III | 350 | D | 72.5 |  | 10193W | 1 | 12.5 | 69 | 59.6 | 71 | 862.5 |  |  | 4 | 12 | CMA7 | ok | type_from_oltc_data
E-CV2260195 巴西WEG.pdf | VCV | E-CV2260195 | 巴西WEG | CV2 | CV2III-350D/145-10193W |  | III | 350 | D | 145 |  | 10193W | 1 | 30 | 138 | 72.46 |  | 1725 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260196 巴西TSEA.pdf | VCV | E-CV2260196 | 巴西TSEA | CV2 | CV2III-350D/145-12231W |  | III | 350 | D | 145 |  | 12231W | 1 | 15 | 138 | 36.2 | 40.3 | 1254.5 |  | 11 |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260197 俄罗斯HMR-JSHC.pdf | VCV | E-CV2260197 | 俄罗斯HMR-JSHC | CV2 | [19 empty] | ok | page_timeout_at_7; no_type
E-CV2260198 巴西WEG.pdf | VCV | E-CV2260198 | 巴西WEG | CV2 | CV2III-350Y/72.5-10193W |  | III | 350 | Y | 72.5 |  | 10193W | 1 | 40 | 138 | 167.3 |  | 996 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260199-202 巴西WEG.pdf | VCV | E-CV2260199-202 | 巴西WEG | CV2 | CV2III-350D/72.5-10193W |  | III | 350 | D | 72.5 |  | 10193W | 4 | 12.5 | 69 | 60.4 |  | 862.5 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260203 俄罗斯HMR-JSHC.pdf | VCV | E-CV2260203 | 俄罗斯HMR-JSHC | CV2 | CV2III-350Y/72.5-10191W |  | III | 350 | Y | 72.5 |  | 10191W | 1 | 63 | 115 | 316.3 | 334 |  |  | 9 |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260204 巴西WEG.pdf | VCV | E-CV2260204 | 巴西WEG | CV2 | CV2III-350D/72.5-10193W |  | III | 350 | D | 72.5 |  | 10193W | 1 | 12.5 | 69 | 60.39 |  | 862.5 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260205-210 哈萨克斯坦 ASIA TRAFO.pdf | VCV | E-CV2260205-210 | 哈萨克斯坦 ASIA TRAFO | CV2 | [8 empty] | 6 | 40 | 110 |  |  | 1958 |  | 9 |  |  | CMA7 | ok | no_type
E-CV2260211 巴西WEG.pdf | VCV | E-CV2260211 | 巴西WEG | CV2 | CV2III-350D/72.5-10193W |  | III | 350 | D | 72.5 |  | 10193W | 1 | 12.5 | 69 | 60.39 |  | 862.5 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260212 巴西WEG.pdf | VCV | E-CV2260212 | 巴西WEG | CV2 | CV2III-350D/72.5-10193W |  | III | 350 | D | 72.5 |  | 10193W | 1 | [10 empty] | ok | po_not_os; type_from_compact
E-CV2260213 印尼HMPI-SINTRA.pdf | VCV | E-CV2260213 | 印尼HMPI-SINTRA | CV2 | CV2III-350D/40.5-10100 | CV2III-350D/40.5-10 | III | 350 | D | 40.5 |  | 10100 | 1 | 1 | 33 | 17.5 | 9.4 | 825 |  | 4 |  |  | SHM-D, SHM-K | ok | type_from_oltc_data
E-CV2260214 缅甸PTE.pdf | VCV | E-CV2260214 | 缅甸PTE | CV2 | CV2III-350D/40.5-10193W |  | III | 350 | D | 40.5 |  | 10193W | 1 | 20 | 33 | 202 | 241.9 | 544.5 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260215-216 印尼GE UNINDO.pdf | VCV | E-CV2260215-216 | 印尼GE UNINDO | CV2 | CV2III-600Y/72.5-10193W |  | III | 600 | Y | 72.5 |  | 10193W | 2 | 140 | 157.5 | 513.2 | 570.2 |  |  | 17 | 8 | 8 | CMA7 | ok | type_from_oltc_data
E-CV2260217 巴西WEG.pdf | VCV | E-CV2260217 | 巴西WEG | CV2 | CV2III-350D/145-10193W |  | III | 350 | D | 145 |  | 10193W | 1 | 26.6 | 138 | 64.26 |  | 1725 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260218 巴西WEG.pdf | VCV | E-CV2260218 | 巴西WEG | CV2 | CV2III-350D/72.5-10193W |  | III | 350 | D | 72.5 |  | 10193W | 1 | 25 | 69 | 120.8 |  | 862.5 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260219 捷克Revos-ZREW.pdf | VCV | E-CV2260219 | 捷克Revos-ZREW | CV2 | CV2III-600Y/72.5-10193W |  | III | 600 | Y | 72.5 |  | 10193W | 1 | 63 | 110 | 330.7 | 393.6 | 1270.2 |  | 8 |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260220 巴西WEG.pdf | VCV | E-CV2260220 | 巴西WEG | CV2 | CV2III-350D/145-10193W |  | III | 350 | D | 145 |  | 10193W | 1 | 40 | 138 | 96.62 |  | 1725 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260221 南非ACTOM.pdf | VCV | E-CV2260221 | 南非ACTOM | CV2 | [8 empty] | 2 | 14 | 66 | 122.5 | 144.1 | 476.3 |  |  |  |  | CMA7 | ok | no_type
E-CV2260222-223土耳其HMT-ZTR.pdf | VCV | E-CV2260222-223 | 土耳其HMT-ZTR | CV2 | CV2III-350Y/72.5-10191W |  | III | 350 | Y | 72.5 |  | 10191W | 2 | 63 | [9 empty] | ok | po_not_os; type_from_compact
E-CV2260224 土耳其HMT-ZTR.pdf | VCV | E-CV2260224 | 土耳其HMT-ZTR | CV2 | CV2III-350Y/72.5-10191W |  | III | 350 | Y | 72.5 |  | 10191W | 1 | 40 | [9 empty] | ok | po_not_os; type_from_compact
E-CV2260225 巴西TRAEL.pdf | VCV | E-CV2260225 | 巴西TRAEL | CV2 | CV2III-350D/145-10193W |  | III | 350 | D | 145 |  | 10193W | 1 | 20 | 138 | 64.3 | 75.6 | 1725 |  |  | 4 | 12 | CMA7 | ok | type_from_oltc_data
E-CV2260226 巴西ITAM.pdf | VCV | E-CV2260226 | 巴西ITAM | CV2 | CV2III-350D/72.5-10193 | CV2III-350D/72.5-10193W | III | 350 | D | 72.5 |  | 10193 | 1 | 9.375 |  |  |  | 862.5 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260227-229 巴西WEG.pdf | VCV | E-CV2260227-229 | 巴西WEG | CV2 | CV2III-350D/40.5-10193W |  | III | 350 | D | 40.5 |  | 10193W | 3 | 7.5 | 34.5 | 72.46 |  | 431.25 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260230 巴西WEG.pdf | VCV | E-CV2260230 | 巴西WEG | CV2 | CV2III-350D/145-10193W |  | III | 350 | D | 145 |  | 10193W | 1 | 6.25 | 138 | 15.1 |  | 1725 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260231-235 巴西WEG.pdf | VCV | E-CV2260231-235 | 巴西WEG | CV2 | CV2III-350D/72.5-10193W |  | III | 350 | D | 72.5 | B | 10193W | 5 | 26.6 | 69 | 128.5 |  | 862.5 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260236-237 巴西WEG.pdf | VCV | E-CV2260236-237 | 巴西WEG | CV2 | CV2III-350D/72.5-10193W |  | III | 350 | D | 72.5 |  | 10193W | 2 | 12.5 | 69 | 60.38 |  | 863 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260238-239 俄罗斯HMR-JSHC.pdf | VCV | E-CV2260238-239 | 俄罗斯HMR-JSHC | CV2 | CV2III-350D/40.5-12233W |  | III | 350 | D | 40.5 |  | 12233W | 2 | 16 | 11 | 126 | 148 |  |  | 10 |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260240-241 俄罗斯HMR-JSHC.pdf | VCV | E-CV2260240-241 | 俄罗斯HMR-JSHC | CV2 | CV2III-350Y/72.5-10193W |  | III | 350 | Y | 72.5 |  | 10193W | 2 | 16 | 36.75 | 252 | 268 | 318 |  | 8 |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260242-243 俄罗斯HMR-JSHC.pdf | VCV | E-CV2260242-243 | 俄罗斯HMR-JSHC | CV2 | CV2III-350Y/72.5-10191W |  | III | 350 | Y | 72.5 |  | 10191W | 2 | 25 | 115 | 125 | 133 | 1182 |  | 9 |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260244 土耳其HMT-ZTR.pdf | VCV | E-CV2260244 | 土耳其HMT-ZTR | CV2 | CV2III-350Y/72.5-10191W |  | III | 350 | Y | 72.5 |  | 10191W | 1 | 40 | [9 empty] | ok | po_not_os; type_from_compact
E-CV2260245-246 土耳其HMT-TASKIN Consultancy.pdf | VCV | E-CV2260245-246 | 土耳其HMT-TASKIN Consultancy | CV2 | CV2III-600Y/40.5-10193W |  | III | 600 | Y | 40.5 |  | 10193W | 2 | 55 | 21 |  | 347.1 | 733.3 |  | 8 |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260247 土耳其HMT-TASKIN Consultancy.pdf | VCV | E-CV2260247 | 土耳其HMT-TASKIN Consultancy | CV2 | CV2III-600D/40.5-12110 |  | III | 600 | D | 40.5 |  | 12110 | 1 | 35 |  | 353.5 | 377.1 | 437.5 |  | 5 |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260248-249 印度TOSHIBA.pdf | VCV | E-CV2260248-249 | 印度TOSHIBA | CV2 | CV2III-600D/72.5-10193G | CV2III-350D/40.5-10100 | III | 600 | D | 72.5 |  | 10193G | 2 | [10 empty] | ok | po_not_os; type_from_compact
E-CV2260250 土耳其HMT-Beta Transformer.pdf | VCV | E-CV2260250 | 土耳其HMT-Beta Transformer | CV2 | CV2III-350Y/72.5-10191W |  | III | 350 | Y | 72.5 |  | 10191W | 1 | 25 | 121 |  | 142.1 | 1243.5 |  | 9 |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260251 印尼Trafoindo.pdf | VCV | E-CV2260251 | 印尼Trafoindo | CV2 | CV2III-350Y/40.5-10193W |  | III | 350 | Y | 40.5 |  | 10193W | 1 | [9 empty] | SHM-D, SHM-K | ok | page_err_10:PdfminerException; po_not_os; type_from_compact
E-CV2260252 越南HLG 售后.pdf | VCV | E-CV2260252 | 越南HLG 售后 | CV2 | CV2III-500Y/72.5-10191W |  | III | 500 | Y | 72.5 |  | 10191W | 1 | [9 empty] | CMA7 | ok | page_timeout_at_8; type_from_compact
E-CV2260253 土耳其HMT-TASKIN Consultancy.pdf | VCV | E-CV2260253 | 土耳其HMT-TASKIN Consultancy | CV2 | CV2III-350Y/72.5-10191G |  | III | 350 | Y | 72.5 |  | 10191G | 1 | 25 | 63 | 230 | 270 | 607 |  | 9 |  |  | ET-SZ6 | ok | type_from_compact
E-CV2260254-256 巴西TRAEL.pdf | VCV | E-CV2260254-256 | 巴西TRAEL | CV2 | CV2III-350D/72.5-10193W |  | III | 350 | D | 72.5 |  | 10193W | 3 | 12.5 | 69 | 59.6 | 71 | 862.5 |  |  | 4 | 12 | CMA7 | ok | type_from_oltc_data
E-CV2260257 巴西TRAEL.pdf | VCV | E-CV2260257 | 巴西TRAEL | CV2 | CV2III-350D/72.5-10193W |  | III | 350 | D | 72.5 |  | 10193W | 1 | 26.6 | 69 | 128.51 | 151.21 | 862.5 |  |  | 4 | 12 | CMA7 | ok | type_from_oltc_data
E-CV2260258 巴西TRAEL.pdf | VCV | E-CV2260258 | 巴西TRAEL | CV2 | CV2III-350D/72.5-10193W |  | III | 350 | D | 72.5 |  | 10193W | 1 | 26.6 | 69 | 128.51 | 151.21 | 862.5 |  |  | 4 | 12 | CMA7 | ok | type_from_oltc_data
E-CV2260259-262 巴西WEG.pdf | VCV | E-CV2260259-262 | 巴西WEG | CV2 | CV2III-350D/145-10193W |  | III | 350 | D | 145 |  | 10193W | 4 | 26.6 | 138 | 64.26 |  | 1725 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260263 巴西WEG.pdf | VCV | E-CV2260263 | 巴西WEG | CV2 | CV2III-350D/145-10193W | CV2III-250D/145-10193W | III | 350 | D | 145 |  | 10193W | 1 | 30 | 138 | 72.46 |  | 1725 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260264-265 巴西WEG.pdf | VCV | E-CV2260264-265 | 巴西WEG | CV2 | CV2III-350D/145-10193W |  | III | 350 | D | 145 |  | 10193W | 2 | 26.6 | 138 | 64.26 | 75.58 | 1725 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260266-267 印度TOSHIBA.pdf | VCV | E-CV2260266-267 | 印度TOSHIBA | CV2 | CV2III-600D/72.5-10193G | CV2III-350D/40.5-10100 | III | 600 | D | 72.5 |  | 10193G | 2 | [10 empty] | ok | po_not_os; type_from_compact
E-CV2260268 智利TUSAN.pdf | VCV | E-CV2260268 | 智利TUSAN | CV2 | CV2III-350D/40.5-10091W |  | III | 350 | D | 40.5 |  | 10091W | 1 | 12.5 | 23 | 181.2 |  | 359 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260269 俄罗斯HMR-JSHC.pdf | VCV | E-CV2260269 | 俄罗斯HMR-JSHC | CV2 | CV2III-350Y/72.5-10191W |  | III | 350 | Y | 72.5 |  | 10191W | 1 | 16 | 115 | 80.3 | 84.9 |  |  | 9 |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260270-271 俄罗斯HMR-SVEL.pdf | VCV | E-CV2260270-271 | 俄罗斯HMR-SVEL | CV2 | CV2III-350Y/72.5-10193W |  | III | 350 | Y | 72.5 |  | 10193W | 2 | 6.3 | 158 | 23 | 24.5 | 1368 |  | 8 |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260272-274 巴西COMTRAFO.pdf | VCV | E-CV2260272-274 | 巴西COMTRAFO | CV2 | CV2III-350D/145-10193W |  | III | 350 | D | 145 |  | 10193W | 3 | 26.6 | 138 | 111.3 | 130.9 | 996 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260275-276 巴西WEG.pdf | VCV | E-CV2260275-276 | 巴西WEG | CV2 | CV2III-350D/145-10193W |  | III | 350 | D | 145 |  | 10193W | 2 | 26.6 | 138 | 64.26 |  | 1725 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260277 土耳其HMT-TASKIN Consultancy.pdf | VCV | E-CV2260277 | 土耳其HMT-TASKIN Consultancy | CV2 | CV2III-600D/72.5-12233W |  | III | 600 | D | 72.5 |  | 12233W | 1 | 52.3 | 33 |  | 603.75 | [6 empty] | ok | type_from_compact
E-CV2260278 巴西WEG.pdf | VCV | E-CV2260278 | 巴西WEG | CV2 | CV2III-600Y/72.5-10193W |  | III | 600 | Y | 72.5 |  | 10193W | 1 | 90 | 138 | 376.53 |  | 1725 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260279-280 巴西WEG.pdf | VCV | E-CV2260279-280 | 巴西WEG | CV2 | CV2III-350D/72.5-10193W |  | III | 350 | D | 72.5 |  | 10193W | 2 | 33.3 | 69 | 160.9 |  | 862.5 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260281 印度TOSHIBA.pdf | VCV | E-CV2260281 | 印度TOSHIBA | CV2 | CV2III-600D/72.5-10193G | CV2III-350D/40.5-10100 | III | 600 | D | 72.5 |  | 10193G | 1 | [10 empty] | ok | po_not_os; type_from_compact
E-CV2260282-283 印度TOSHIBA.pdf | VCV | E-CV2260282-283 | 印度TOSHIBA | CV2 | CV2III-600D/72.5-10193G | CV2III-350D/40.5-10100 | III | 600 | D | 72.5 |  | 10193G | 2 | [9 empty] | CMA7 | ok | po_not_os; type_from_compact
E-CV2260284 土耳其HMT-TASKIN Consultancy.pdf | VCV | E-CV2260284 | 土耳其HMT-TASKIN Consultancy | CV2 | CV2III-600D/40.5-12233W |  | III | 600 | D | 40.5 |  | 12233W | 1 | 51.75 | [8 empty] | CMA7 | ok | po_not_os; type_from_compact
E-CV2260285 巴西WEG.pdf | VCV | E-CV2260285 | 巴西WEG | CV2 | CV2III-350D/40.5-10193W |  | III | 350 | D | 40.5 |  | 10193W | 1 | 7.5 | 34.5 | 72.46 |  | 431.25 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260286 华明印尼TPP.pdf | VCV | E-CV2260286 | 华明印尼TPP | CV2 | CV2III-600D/40.5-10091W |  | III | 600 | D | 40.5 |  | 10091W | 1 | [9 empty] | SHM-D, SHM-K | ok | po_not_os; type_from_compact
E-CV2260287 巴西WEG.pdf | VCV | E-CV2260287 | 巴西WEG | CV2 | CV2III-350D/145-10193W |  | III | 350 | D | 145 |  | 10193W | 1 | 30 | 138 | 72.46 |  | 1725 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260288 华明印尼TPP.pdf | VCV | E-CV2260288 | 华明印尼TPP | CV2 | CV2III-600D/40.5-10193W |  | III | 600 | D | 40.5 |  | 10193W | 1 | [9 empty] | SHM-D, SHM-K | ok | po_not_os; type_from_compact
E-CV2260289 巴西Dentsitel.pdf | VCV | E-CV2260289 | 巴西Dentsitel | CV2 | CV2III-350D/145-10193W | CV2III-350D/72.5-10193W | III | 350 | D | 145 |  | 10193W | 1 |  | 138 | 62.76 | [6 empty] | CMA7 | ok | type_from_oltc_data
E-CV2260290-291 俄罗斯HMR-UETM.pdf | VCV | E-CV2260290-291 | 俄罗斯HMR-UETM | CV2 | CV2III-600Y/72.5-10193W |  | III | 600 | Y | 72.5 |  | 10193W | 2 | 32 | 36.75 | 503 | 535 | 318 |  | 8 |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260292-293 印度TOSHIBA.pdf | VCV | E-CV2260292-293 | 印度TOSHIBA | CV2 | CV2III-600D/72.5-10193G | CV2III-600D/40.5-10193G | III | 600 | D | 72.5 |  | 10193G | 2 | [9 empty] | CMA7 | ok | po_not_os; type_from_compact
E-CV2260294-295 印度TOSHIBA.pdf | VCV | E-CV2260294-295 | 印度TOSHIBA | CV2 | CV2III-600D/72.5-10193G | CV2III-600D/40.5-10193G | III | 600 | D | 72.5 |  | 10193G | 2 | [9 empty] | CMA7 | ok | po_not_os; type_from_compact
E-CV2260296 南非ACTOM.pdf | VCV | E-CV2260296 | 南非ACTOM | CV2 | CV2III-600D/126-10193W |  | III | 600 | D | 126 |  | 10193W | 1 | 80 | 132 | 349.9 | 411.66 | 952.63 |  |  |  |  | CMA7 | ok | type_from_compact
E-CV2260297 南非ACTOM.pdf | VCV | E-CV2260297 | 南非ACTOM | CV2 | CV2III-600D/725-10193W |  | III | 600 | D | 725 |  | 10193W | 1 | 80 | 132 | 349.9 | 411.66 | 952.63 |  |  |  |  | CMA7 | ok | type_from_compact
E-CV2260298 印尼GE UNINDO.pdf | VCV | E-CV2260298 | 印尼GE UNINDO | CV2 | CV2III-350D/72.5-12233W |  | III | 350 | D | 72.5 |  | 12233W | 1 | 24 | 60 | 115.94 | 133.27 | 897 |  | 10 |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260299-304 土耳其HMT-TASKIN Consultancy.pdf | VCV | E-CV2260299-304 | 土耳其HMT-TASKIN Consultancy | CV2 | CV2III-600Y/72.5-10191W |  | III | 600 | Y | 72.5 |  | 10191W | 6 | 50 | [8 empty] | CMA7 | ok | po_not_os; type_from_compact
E-CV2260305-307 巴西COMTRAFO.pdf | VCV | E-CV2260305-307 | 巴西COMTRAFO | CV2 | CV2III-350D/72.5-10193W |  | III | 350 | D | 72.5 |  | 10193W | 3 | 20 | 69 | 167.3 | 196.9 | 498 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260308 巴西WEG.pdf | VCV | E-CV2260308 | 巴西WEG | CV2 | CV2III-350D/145-10193W |  | III | 350 | D | 145 |  | 10193W | 1 | 26.6 | 138 | 64.26 |  | 1725 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260309-312 巴西WEG.pdf | VCV | E-CV2260309-312 | 巴西WEG | CV2 | CV2III-350D/145-10193W |  | III | 350 | D | 145 |  | 10193W | 4 | 33.3 | 138 | 80.43 |  | 1725 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260313 意大利GETRA-ENEL.pdf | VCV | E-CV2260313 | 意大利GETRA-ENEL | CV2 | CV2III-350Y/40.5-10193G |  | III | 350 | Y | 40.5 |  | 10193G | 1 | 10 | 20.8 | 277.6 |  | 150 |  |  |  |  | CMA7 | ok | page_timeout_at_11; type_from_oltc_data
E-CV2260314 美国HMUS-C.E.M..pdf | VCV | E-CV2260314 | 美国HMUS-C.E.M. | CV2 | CV2III-350D/40.5-10100 |  | III | 350 | D | 40.5 |  | 10100 | 1 | 10 | 13.8 | 241.6 |  |  | 910 |  |  | 9 | CMA7 | ok | type_from_oltc_data
E-CV2260315-316 俄罗斯HMR-JSHC.pdf | VCV | E-CV2260315-316 | 俄罗斯HMR-JSHC | CV2 | CV2III-350Y/72.5-10191W |  | III | 350 | Y | 72.5 |  | 10191W | 2 | 40 | 115 | 201 | 212 | 1182 |  | 9 |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260317-318 巴西TRAEL.pdf | VCV | E-CV2260317-318 | 巴西TRAEL | CV2 | CV2III-350D/145-10193W | CV2III-350D/72.5-12231W ¦ CV2III-350D/145-12231W | III | 350 | D | 145 |  | 10193W | 2 | 25 | 138 | 60.4 | 71 | 1725 |  |  | 4 | 12 | CMA7 | ok | type_from_oltc_data
E-CV2260319-320 巴西COMTRAFO.pdf | VCV | E-CV2260319-320 | 巴西COMTRAFO | CV2 | CV2III-350D/72.5-10193W |  | III | 350 | D | 72.5 |  | 10193W | 2 | 20 | 69 | 167.3 | 196.9 | 498 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260321 巴西DATA.pdf | VCV | E-CV2260321 | 巴西DATA | CV2 | CV2III-350D/126-10193W |  | III | 350 | D | 126 | C | 10193W | 1 | 60 |  | 263 | [6 empty] | CMA7 | ok | type_from_oltc_data
E-CV2260322-325 土耳其HMT-TASKIN Consultancy.pdf | VCV | E-CV2260322-325 | 土耳其HMT-TASKIN Consultancy | CV2 | CV2III-600Y/72.5-10191W |  | III | 600 | Y | 72.5 |  | 10191W | 4 | 50 |  | 458.2 |  | 606.3 |  |  |  |  | CMA7 | ok | po_not_os; type_from_compact
E-CV2260326 俄罗斯HMR-SIEMENS.pdf | VCV | E-CV2260326 | 俄罗斯HMR-SIEMENS | CV2 | [19 empty] | scanned_or_empty | page_timeout_at_8
E-CV2260327 土耳其HMT-TASKIN Consultancy.pdf | VCV | E-CV2260327 | 土耳其HMT-TASKIN Consultancy | CV2 | CV2III-350Y/72.5-10191W |  | III | 350 | Y | 72.5 |  | 10191W | 1 | 50 | 132 | 218.7 | 257.3 | 1271 |  | 9 |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260328 巴西WEG 售后.pdf | VCV | E-CV2260328 | 巴西WEG 售后 | CV2 | [19 empty] | ok | no_type
E-CV2260329-334 缅甸PTE.pdf | VCV | E-CV2260329-334 | 缅甸PTE | CV2 | CV2III-350D/40.5-10193W |  | III | 350 | D | 40.5 |  | 10193W | 6 | [9 empty] | CMA7 | ok | page_timeout_at_12; po_not_os; type_from_compact
E-CV2260335-336 巴西TRAEL.pdf | VCV | E-CV2260335-336 | 巴西TRAEL | CV2 | CV2III-350D/145-12231W | CV2III-350D/72.5-10193W ¦ CV2III-350D/72.5-12231W ¦ CV2III-350D/145-10193W | III | 350 | D | 145 |  | 12231W | 3 | 33 | 84 | 226.8 | 252 | 763.6 |  | 11 |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260337 巴西TRAEL.pdf | VCV | E-CV2260337 | 巴西TRAEL | CV2 | CV2III-350D/145-12231W | CV2III-350D/72.5-12231W ¦ CV2III-350D/145-10193W | III | 350 | D | 145 |  | 12231W | 1 | 25 | 138 | 104.6 | 116.2 | 1255 |  | 11 |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260338 巴西TRAEL.pdf | VCV | E-CV2260338 | 巴西TRAEL | CV2 | CV2III-350D/72.5-12231W | CV2III-350D/145-10193W ¦ CV2III-350D/145-12231W | III | 350 | D | 72.5 |  | 12231W | 1 | 20 | 69 | 167.3 | 185.9 | 627.5 |  | 11 |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260339 越南Chengyang Paper 售后.pdf | VCV | E-CV2260339 | 越南Chengyang Paper 售后 | CV2 | CV2III-500Y/72.5-10193W |  | III | 500 | Y | 72.5 |  | 10193W | 1 | [10 empty] | ok | page_timeout_at_6; type_from_compact
E-CV2260340 巴西TRAEL.pdf | VCV | E-CV2260340 | 巴西TRAEL | CV2 | CV2III-350D/72.5-12231W | CV2III-350D/145-10193W ¦ CV2III-350D/145-12231W | III | 350 | D | 72.5 |  | 12231W | 1 | 20 | 69 | 167.3 | 185.9 | 627.5 |  | 11 |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260341-342 越南SANAKY 600D.pdf | VCV | E-CV2260341-342 | 越南SANAKY 600D | CV2 | CV2III-600D/40.5-10193W | CV2III-350D/40.5-10193W | III | 600 | D | 40.5 |  | 10193W | 2 | 26 | 22 | 394 | 438 | 275 |  | 8 |  |  | CMA7, SHM-K | ok | type_from_oltc_data
E-CV2260343-344 越南SANAKY 350D.pdf | VCV | E-CV2260343-344 | 越南SANAKY 350D | CV2 | CV2III-350D/40.5-10193W | CV2III-600D/40.5-10193W | III | 350 | D | 40.5 |  | 10193W | 2 | 26 | 22 | 152 | 168 | 275 |  | 8 |  |  | CMA7, SHM-K | ok | type_from_oltc_data
E-CV2260345 巴西WEG.pdf | VCV | E-CV2260345 | 巴西WEG | CV2 | CV2III-350D/145-10193W |  | III | 350 | D | 145 |  | 10193W | 1 | 26.6 | 138 | 64.26 |  | 1725 |  |  |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260346 土耳其HMT-Green Transfo.pdf | VCV | E-CV2260346 | 土耳其HMT-Green Transfo | CV2 | CV2III-600Y/72.5-10173G |  | III | 600 | Y | 72.5 |  | 10173G | 1 | 40 | 64 | 360.8 | 419.6 | 739 |  | 7 |  |  | CMA7 | ok | type_from_oltc_data
E-CV2260349 印尼HMPI 型式试验.pdf | VCV | E-CV2260349 | 印尼HMPI 型式试验 | CV2 | [19 empty] | scanned_or_empty
E-WG260001 乌兹别克斯坦CHIRCHIK.pdf | WG | E-WG260001 | 乌兹别克斯坦CHIRCHIK | WSG | WDGV-800Y/40.5-6x5 |  | V | 800 | Y | 40.5 |  | 6x5 | 1 |  |  |  |  | 555.7 | [5 empty] | ok | po_not_os; type_from_os_row
E-WG260002-003 乌兹别克斯坦CHIRCHIK.pdf | WG | E-WG260002-003 | 乌兹别克斯坦CHIRCHIK | WSG | WDGV-800/40.5-6x5B | WDGV-800Y/40.5-6x5 | V | 800 |  | 40.5 |  | 6x5B | 2 |  |  |  |  | 555.7 | [5 empty] | ok | po_not_os; type_from_compact
E-WG260004-009 俄罗斯HMR-TOGLIATTI.pdf | WG | E-WG260004-009 | 俄罗斯HMR-TOGLIATTI | WSG | WDGIV-800/40.5-5x5A | CVIII-350Y/72.5-10191W | IV | 800 |  | 40.5 |  | 5x5A | 6 | 40 | 38.5 | 600 | 631 |  |  | 2 |  |  | CMA7 | ok | type_from_oltc_data
E-WG260010-012 俄罗斯HMR-TOGLIATTI.pdf | WG | E-WG260010-012 | 俄罗斯HMR-TOGLIATTI | WSG | 3xWDGIV-400/40.5-5x5A | CMIII-500Y/72.5B-10193W ¦ WDGIV-400/40.5-5x5A | IV | 400 |  | 40.5 |  | 5x5A | 3 | 25 | 38.5 | 374.9 | 394.6 |  |  | 2 |  |  | CMA7 | ok | type_from_oltc_data
E-WG260013-014 乌兹别克斯坦CHIRCHIK.pdf | WG | E-WG260013-014 | 乌兹别克斯坦CHIRCHIK | WSG | WDGV-800Y/40.5-6x5 | WDGV-800/40.5-6x58 ¦ WDGV-800/40.5-6x5 | V | 800 | Y | 40.5 |  | 6x5 | 2 |  |  |  |  | 555.7 | [5 empty] | ok | po_not_os; type_from_os_row
E-WG260015-016.pdf | WG | E-WG260015-016 |  | WSG | 3xWDGIV-400/72.5-5x5A | 3xWDGIV-400/72.5-5x5 ¦ WDGIV-400/72.5-5x5A | IV | 400 |  | 72.5 | A | 5x5 | 3 | 25 | 38.5 | 375 | 395 |  |  | 2 |  |  |  | ok | type_from_oltc_data
E-WG260017-018 俄罗斯HMR-TOGLIATTI.pdf | WG | E-WG260017-018 | 俄罗斯HMR-TOGLIATTI | WSG | 3xWDGIV-400/40.5-5x5A | CMIII-500Y/72.5B-10193W ¦ WDGIV-400/40.5-5x5A | IV | 400 |  | 40.5 |  | 5x5A | 3 | 25 | 38.5 | 374.9 | 394.6 |  |  | 2 |  |  | CMA7 | ok | type_from_oltc_data
E-WG260019 俄罗斯HMR-JSHC.pdf | WG | E-WG260019 | 俄罗斯HMR-JSHC | WSG | 3xWDGIV-800/72.5-5x5A | CMIII-500Y/72.5B-10193W ¦ 3xWDGIV-800/72.5-5x5 ¦ WDGIV-800/72.5-5x5A | IV | 800 |  | 72.5 | A | 5x5 | 3 | 40 | 38.5 | 600.6 | 630.6 |  |  | 2 |  |  |  | ok | type_from_oltc_data
E-WG260020 哈萨克斯坦 ASIA TRAFO .pdf | WG | E-WG260020 | 哈萨克斯坦 ASIA TRAFO | WSG | 3xWDGIV-400/72.5-5x5A | WDGIV-400/72.5-5x5A | IV | 400 |  | 72.5 | A | 5x5 | 3 | 25 | 38.5 | 375 | 395 |  |  | 2 |  |  |  | ok | type_from_os_row
E-WG260021-022 俄罗斯HMR-JSHC.pdf | WG | E-WG260021-022 | 俄罗斯HMR-JSHC | WSG | 3xWDGIV-400/72.5-5x5A | CMIII-500Y/72.5B-10193W ¦ 3xWDGIV-400/72.5-5x5 ¦ WDGIV-400/72.5-5x5A | IV | 400 |  | 72.5 | A | 5x5 | 3 | 25 | 38.5 | 375 | 395 |  |  | 2 |  |  | CMA7 | ok | type_from_oltc_data
E-WG260023 乌兹别克斯坦CHIRCHIQ.pdf | WG | E-WG260023 | 乌兹别克斯坦CHIRCHIQ | WSG | WDGV-800/40.5-6x5 |  | V | 800 |  | 40.5 |  | 6x5 | 1 | 6.3 | 36.75 | [5 empty] | 4 | 4 |  | ok | type_from_compact
E-WG260024-026 俄罗斯HMR-TOGLIATTI.pdf | WG | E-WG260024-026 | 俄罗斯HMR-TOGLIATTI | WSG | WDGIV-800/40.5-5x5A |  | IV | 800 |  | 40.5 |  | 5x5A | 3 | 40 | 38.5 | 600 | 631 |  |  | 2 |  |  |  | ok | type_from_oltc_data
E-WG260027 哈萨克斯坦 ASIA TRAFO .pdf | WG | E-WG260027 | 哈萨克斯坦 ASIA TRAFO | WSG | 3xWDGIV-400/72.5-5x5A | WDGIV-400/72.5-5x5A | IV | 400 |  | 72.5 | A | 5x5 | 3 | 25 | 38.5 | 375 | 395 |  |  | 2 |  |  |  | ok | type_from_os_row
E-WG260028-030 哈萨克斯坦ASIATRAFO .pdf | WG | E-WG260028-030 | 哈萨克斯坦ASIATRAFO | WSG | [8 empty] | 2 | [6 empty] | 1 |  |  | SHM-D | ok | no_type
E-WG260031-032 俄罗斯HMR-JSHC.pdf | WG | E-WG260031-032 | 俄罗斯HMR-JSHC | WSG | CVIII-350Y/72.5-10191W | 3xWDGIV-300/72.5-5x5B | III | 350 | Y | 72.5 |  | 10191W | 2 | 16 | 38.5 | 239.9 | 252.6 | [5 empty] | CMA7 | ok | type_from_compact
E-WG260033 俄罗斯HMR-JSHC.pdf | WG | E-WG260033 | 俄罗斯HMR-JSHC | WSG | [19 empty] | ok | page_timeout_at_7; no_type
E-WG260034 俄罗斯HMR-JSHC.pdf | WG | E-WG260034 | 俄罗斯HMR-JSHC | WSG | 3xWDGV-800/72.5-6x5B |  | V | 800 |  | 72.5 |  | 6x5B | 3 | 125 | 121 | 596.4 | 627.8 |  |  | 2 |  |  |  | ok | page_timeout_at_8; type_from_oltc_data
E-WG260035-040 俄罗斯HMR-TOGLIATTI.pdf | WG | E-WG260035-040 | 俄罗斯HMR-TOGLIATTI | WSG | WDGIV-800/40.5-5x5A |  | IV | 800 |  | 40.5 |  | 5x5A | 6 | 40 | 38.5 | 600 | 631 |  |  | 2 |  |  |  | ok | type_from_oltc_data
E-WG260041 哈萨克斯坦 ASIA TRAFO .pdf | WG | E-WG260041 | 哈萨克斯坦 ASIA TRAFO | WSG | 3xWDGIV-400/72.5-5x5A | WDGIV-400/72.5-5x5A | IV | 400 |  | 72.5 | A | 5x5 | 3 | 25 | 38.5 | 375 | 395 |  |  | 2 |  |  |  | ok | type_from_os_row
E-WG260042-043 俄罗斯HMR-JSHC.pdf | WG | E-WG260042-043 | 俄罗斯HMR-JSHC | WSG | 3xWDGIV-800/72.5-5x5A | 3xWDGIV-800/72.5-5x5 ¦ WDGIV-800/72.5-5x5A | IV | 800 |  | 72.5 | A | 5x5 | 3 | 40 | 38.5 | 600.6 | 630.6 |  |  | 2 |  |  |  | ok | type_from_oltc_data
E-WG260044 俄罗斯HMR-JSHC.pdf | WG | E-WG260044 | 俄罗斯HMR-JSHC | WSG | 3xWDGIV-1250/72.5-5x5A | WDGIV-1250/72.5-5x5A ¦ WDGIV-1250/72.5-12 | IV | 1250 |  | 72.5 | A | 5x5 | 3 | 63 | 38.5 | 945 | 995 |  |  | 2 |  |  |  | ok | type_from_oltc_data
E-WG260045 俄罗斯HMR-TOGLIATTI.pdf | WG | E-WG260045 | 俄罗斯HMR-TOGLIATTI | WSG | 3xWDGIV-400/40.5-5x5A | 3xWDGIV-400/72.5-5x5A ¦ 3xWDGIV-400/72.5-5x5 | IV | 400 |  | 40.5 |  | 5x5A | 3 | 25 | 38.5 | 374.9 | 394.6 |  |  | 2 |  |  | SHM-DL | ok | type_from_oltc_data
E-W260001 俄罗斯HMR-Podolsk.pdf | WL | E-W260001 | 俄罗斯HMR-Podolsk | WSL | WSLIV-600D/72.5-6x5B | WSLIV-600Y/72.5-6x5B ¦ WSLIV-600D/72.5-6x5 ¦ WSLIV-600Y/72.5-6x5 | IV | 600 | D | 72.5 | B | 6x5 | 1 | 9.37 | 10.5 | 297 | 297 |  |  |  |  | 4 |  | ok | type_from_oltc_data
E-W260002 俄罗斯HMR-Podolsk.pdf | WL | E-W260002 | 俄罗斯HMR-Podolsk | WSL | WSLIV-600Y/72.5-6x5B | WSLIV-600D/72.5-6x5B ¦ WSLIV-600D/72.5-6x5 ¦ WSLIV-600Y/72.5-6x5 | IV | 600 | Y | 72.5 | B | 6x5 | 1 | 9.37 | 10.5 | 515 | 515 |  |  |  |  | 4 |  | ok | type_from_oltc_data
E-W260003 越南 EEMC.pdf | WL | E-W260003 | 越南 EEMC | WSL | WSLIV-600Y/72.5-6x5A | WSLII-800D/72.5-6x5A | IV | 600 | Y | 72.5 |  | 6x5A | 1 | 25 | 115 | 125.6 | 132.2 |  |  | 2 |  |  | CMA7 | ok | type_from_compact
E-W260004-006 越南 EEMC.pdf | WL | E-W260004-006 | 越南 EEMC | WSL | WSLIV-600Y/72.5-6x5A | WSLII-800D/72.5-6x5A | IV | 600 | Y | 72.5 |  | 6x5A | 3 | [10 empty] | ok | type_from_compact
E-W260007 印尼GE.pdf | WL | E-W260007 | 印尼GE | WSL | WSLIV-800Y/170-6x5B |  | IV | 800 | Y | 170 |  | 6x5B | 2 | 153.75 | 157.5 | 563.6 | 592.81 |  |  | 2 |  |  | CMA7 | ok | type_from_compact
E-W260008-009 美国 HMUS-HOWARD.pdf | WL | E-W260008-009 | 美国 HMUS-HOWARD | WSL | WDLIV-600/72.5-17x16E | WDLIV-600/72.5-17x1 | IV | 600 |  | 72.5 | E | 17x16 | 2 |  | 24 | 150 | 150 |  |  | 16 |  |  |  | ok | type_from_octc
E-W260010 俄罗斯HMR-SIEMENS.pdf | WL | E-W260010 | 俄罗斯HMR-SIEMENS | WSL | WSLIV-800Y/72.5-6x5A | WSLIV-800Y/72.5-6x5 | IV | 800 | Y | 72.5 | A | 6x5 | 1 | 40 | 38.5 | 599.8 | 631.4 |  |  | 2 |  |  |  | ok | type_from_oltc_data
E-W260011 俄罗斯HMR-SIEMENS.pdf | WL | E-W260011 | 俄罗斯HMR-SIEMENS | WSL | WSLIV-1600Y/72.5-6x5 | WSLIV-1600Y/72.5-6x5A | IV | 1600 | Y | 72.5 |  | 6x5 | 1 | 63 | 38.5 | 944.8 | 994.5 |  |  | 2 |  |  |  | ok | type_from_oltc_data
E-W260012 越南EEMC.pdf | WL | E-W260012 | 越南EEMC | WSL | WSLII-2000Y/72.5-6x5B | WSLII-600Y/72.5-6x5A | II | 2000 | Y | 72.5 |  | 6x5B | 1 | 50 | 23 | 1256 | 1323 | 332 |  | 2 |  |  | CMA7 | ok | type_from_compact
E-W260013 越南EEMC.pdf | WL | E-W260013 | 越南EEMC | WSL | WSLII-2000Y/72.5-6x5B | WSLII-600Y/72.5-6x5A | II | 2000 | Y | 72.5 |  | 6x5B | 1 | 80 | 230 | 201 | 212 | 3320 |  | 2 |  |  | CMA7 | ok | type_from_compact
E-W260014-015 捷克Revos-ZREW.pdf | WL | E-W260014-015 | 捷克Revos-ZREW | WSL | WSLIV-800D/72.5-6x5A |  | IV | 800 | D | 72.5 |  | 6x5A | 1 | 40 | 22 | 1049.7 | 637.9 | 550 |  | 2 |  |  | CMA7 | ok | type_from_compact
E-W260016-017 俄罗斯HMR-SIEMENS.pdf | WL | E-W260016-017 | 俄罗斯HMR-SIEMENS | WSL | [8 empty] | 2 | [10 empty] | ok | page_timeout_at_7; no_type
E-W260018 越南MEE.pdf | WL | E-W260018 | 越南MEE | WSL | [19 empty] | ok | po_not_os; no_type
E-W260019 土耳其HMT-Eren Transformer.pdf | WL | E-W260019 | 土耳其HMT-Eren Transformer | WSL | CMIII-600Y/72.5C-14271G |  | III | 600 | Y | 72.5 | C | 14271G | 1 | 2.5 | 5 | [8 empty] | ok | type_from_compact
E-W260020 越南EEMC.pdf | WL | E-W260020 | 越南EEMC | WSL | WSLII-800D/72.5-6x5A |  | II | 800 | D | 72.5 |  | 6x5A | 1 | [10 empty] | ok | type_from_compact
E-W260021 韩国CHERYONG.pdf | WL | E-W260021 | 韩国CHERYONG | WSL | [9 empty] | 10 |  | 152 | 303 |  |  |  | 50 | 2 |  | ok | no_type
E-W260022-023 美国HMUS-HOWARD.pdf | WL | E-W260022-023 | 美国HMUS-HOWARD | WSL | WDLIV-1200/72.5-9x8E | WDLIV-1200/72.5-9x8 | IV | 1200 |  | 72.5 | E | 9x8 | 4 | 1 | 24 | 1000 | 1000 |  |  | 8 |  |  | CMA7 | ok | type_from_octc
E-W260024-025 韩国KP ELECTRIC.pdf | WL | E-W260024-025 | 韩国KP ELECTRIC | WSL | [8 empty] | 2 | 0.15 |  | 600 | 600 |  |  |  | 6 | 1 |  | ok | no_type
E-W260026-027 俄罗斯HMR-SIEMENS.pdf | WL | E-W260026-027 | 俄罗斯HMR-SIEMENS | WSL | [19 empty] | scanned_or_empty | page_timeout_at_7
E-W260028 捷克Revos-ZREW.pdf | WL | E-W260028 | 捷克Revos-ZREW | WSL | WSLIV-600D/72.5-6x5A |  | IV | 600 | D | 72.5 |  | 6x5A | 1 | 16 | 22 | 419.9 | 255.2 | 550 |  | 2 |  |  | CMA7 | ok | type_from_compact
E-W260029 越南HLG 售后.pdf | WL | E-W260029 | 越南HLG 售后 | WSL | [19 empty] | ok | po_not_os; no_type
E-W260030-031 俄罗斯HMR-SIEMENS.pdf | WL | E-W260030-031 | 俄罗斯HMR-SIEMENS | WSL | WSLV-800D/126-6x5A | WSLV-800D/126-6x5 | V | 800 | D | 126 | A | 6x5 | 1 | 250 | 242 | 596.4 | 627.8 |  |  | 2 |  |  |  | ok | type_from_oltc_data
E-W260032,E-W260037 俄罗斯HMR-SIEMENS.pdf | WL | E-W260032,E-W260037 | 俄罗斯HMR-SIEMENS | WSL | [8 empty] | 2 | [10 empty] | ok | page_timeout_at_7; no_type
E-W260033-034 越南EEMC.pdf | WL | E-W260033-034 | 越南EEMC | WSL | WSLII-800D/72.5-6x5A |  | II | 800 | D | 72.5 |  | 6x5A | 2 | [10 empty] | ok | po_not_os; type_from_compact
E-W260035 越南Sanaky.pdf | WL | E-W260035 | 越南Sanaky | WSL | WSLII-600D/72.5-12x11C | WSLII-600D/72.5-12x1 | II | 600 | D | 72.5 | C | 12x11 | 1 | 18.75 | 67 | 161.6 | 185 | 1675 |  | 5 | 5 | 5 | CMA7 | ok | type_from_octc
E-W260036 捷克Revos-ZREW.pdf | WL | E-W260036 | 捷克Revos-ZREW | WSL | WSLIV-600D/72.5-6x5A |  | IV | 600 | D | 72.5 |  | 6x5A | 1 | 16 | 22 | 419.9 | 255.2 | 550 |  | 2 |  |  | CMA7 | ok | type_from_compact
E-W260038 俄罗斯HMR-JSCLPM.pdf | WL | E-W260038 | 俄罗斯HMR-JSCLPM | WSL | WSLIV-600Y/72.5-6x5A | WSLIV-600Y/72.5-6x5 | IV | 600 | Y | 72.5 | A | 6x5 | 1 | 25 | 38.5 | 375 | 395 |  |  | 2 |  |  |  | ok | type_from_oltc_data
E-W260039 美国HMUS-C.E.M..pdf | WL | E-W260039 | 美国HMUS-C.E.M. | WSL | WSLIV-1600D/72.5-7x6D | WSLIV-1600D/72.5-7x6 ¦ CM2I-1500/72.5B-18180 | IV | 1600 | D | 72.5 | D | 7x6 | 1 | 7.389 | 13.8 | 1014.5 | 1217.4 |  |  |  | 7 |  | CMA7 | ok | type_from_octc
E-W260040 越南EEMC.pdf | WL | E-W260040 | 越南EEMC | WSL | WSLII-800D/72.5-6x5A |  | II | 800 | D | 72.5 |  | 6x5A | 1 | [10 empty] | ok | po_not_os; type_from_compact
E-W260041-042 俄罗斯HMR-SIEMENS.pdf | WL | E-W260041-042 | 俄罗斯HMR-SIEMENS | WSL | WSLVIII-800D/72.5-5x2B | WSLVIII-800D/72.5-5x2 | VIII | 800 | D | 72.5 | B | 5x2 | 2 | 25 |  | 794 | 794 | [6 empty] | ok | type_from_oltc_data
E-W260043-044 俄罗斯HMR-SIEMENS.pdf | WL | E-W260043-044 | 俄罗斯HMR-SIEMENS | WSL | WSLIV-600Y/72.5-6x5A | WSLIV-600Y/72.5-6x5 | IV | 600 | Y | 72.5 | A | 6x5 | 2 | 25 | 38.5 | 375 | 395 |  |  | 2 |  |  |  | ok | type_from_oltc_data
E-W260045 俄罗斯HMR-PMTT.pdf | WL | E-W260045 | 俄罗斯HMR-PMTT | WSL | WSLIV-600D/126-6x5D | WSLIV-600D/126-6x5 | IV | 600 | D | 126 | D | 6x5 | 1 | 250 | 525 | 274.9 | 289.4 |  |  | 2 |  |  |  | ok | type_from_oltc_data
E-W260046 俄罗斯HMR-SIEMENS.pdf | WL | E-W260046 | 俄罗斯HMR-SIEMENS | WSL | WSLIV-600Y/72.5-6x5A | WSLIV-600Y/72.5-6x5 | IV | 600 | Y | 72.5 | A | 6x5 | 1 | 25 | 558 | 375 | 395 |  |  | 2 |  |  |  | ok | type_from_octc

## summary
folder | files | with_sold_type | with_i | with_mva | scanned_or_empty | parse_failed | type_rate
CM | 84 | 66 | 45 | 68 | 1 | 0 | 0.786
CMD | 8 | 7 | 7 | 7 | 0 | 0 | 0.875
CV | 159 | 104 | 87 | 104 | 3 | 0 | 0.654
CVT | 4 | 2 | 3 | 1 | 1 | 0 | 0.5
CZ | 12 | 8 | 8 | 7 | 0 | 0 | 0.667
HWV | 7 | 6 | 6 | 6 | 0 | 0 | 0.857
SHZV | 44 | 35 | 28 | 37 | 1 | 0 | 0.795
SY | 18 | 13 | 6 | 7 | 1 | 0 | 0.722
VCM | 88 | 71 | 58 | 67 | 3 | 0 | 0.807
VCV | 196 | 183 | 150 | 162 | 3 | 0 | 0.934
WG | 22 | 20 | 16 | 17 | 0 | 0 | 0.909
WL | 33 | 26 | 23 | 23 | 1 | 0 | 0.788
TOTAL | 675 | 541 | 437 | 506 | 14 | 0 | 0.801

## replay
serial | folder | sold_type | engine_primary | engine_next | verdict | skip_reason | i_duty | um | ust | steps | connection | phases | miss_note
E-M260001 | CM | CMIII-600Y/72.5C-14253W | CM2III-600Y/72.5B-12231W | SHZVIII-600Y/72.5B-12231W ¦ SHZVIII-1000Y/72.5B-12231W ¦ SHZVGIII-1300Y/72.5B-12231W | eligible |  | 533.5 | 72.5 | 1976.7 | 11 | Y | III
E-M260002-003 | CM |  |  |  | skip | no sold_type
E-M260004-005 | CM |  |  |  | skip | no sold_type
E-M260006-007 | CM |  |  |  | skip | no sold_type
E-M260008 | CM | CMIII-500Y/72.5B-10193W | CV2III-350Y/72.5-10193W | CV2III-600Y/72.5-10193W ¦ CVIII-350Y/72.5-10193W ¦ SVIII-500Y/72.5-10193W | eligible |  | 155.5 | 72.5 | 1368 | 8 | Y | III
E-M260009 | CM | CMIII-500Y/126C-10193G |  |  | skip | no transformer I |  | 126 |  |  | Y | III
E-M260010 | CM | CMIII-500Y/72.5C-16150 |  |  | skip | no transformer I |  | 72.5 | 3000 |  | Y | III
E-M260011-013 | CM | CMIII-500Y/72.5B-10193W | CV2III-350Y/72.5-10193W | CV2III-600Y/72.5-10193W ¦ CVIII-350Y/72.5-10193W ¦ SVIII-500Y/72.5-10193W | eligible |  | 97.2 | 72.5 | 1368 | 8 | Y | III
E-M260014-015 | CM | CMIII-500Y/72.5B-10193W | CV2III-350Y/72.5-10193W | CV2III-600Y/72.5-10193W ¦ CVIII-350Y/72.5-10193W ¦ SVIII-500Y/72.5-10193W | eligible |  | 97.2 | 72.5 | 1368 | 8 | Y | III
E-M260016 | CM | 3xCMI-1200/170C-14131W | CM2I-800/170D-14131W | CM2I-1200/170D-14131W ¦ SHZVI-1000/170D-14131W ¦ SHZVI-1200/170D-14131W | eligible |  | 747.4 | 170 | 1824 | 6 | Y | I
E-M260017 | CM |  |  |  | skip | no sold_type
E-M260018-019 | CM |  |  |  | skip | no sold_type
E-M260020 | CM |  |  |  | skip | no sold_type
E-M260021 | CM | CMIII-500Y/72.5B-10080 | CV2III-350Y/72.5-10080 | CV2III-600Y/72.5-10080 ¦ CVIII-350Y/72.5-10080 ¦ SVIII-500Y/72.5-10080 | eligible |  | 314.9 | 72.5 | 927 |  | Y | III
E-M260022 | CM |  |  |  | skip | no sold_type
E-M260023-024 | CM | 3xCMI-800/170C-14131W | CM2I-800/170D-14131W | CM2I-1200/170D-14131W ¦ SHZVI-1000/170D-14131W ¦ SHZVI-1200/170D-14131W | eligible |  | 634.5 | 170 | 1397 | 6 | Y | I
E-M260025 | CM | CMI-1200/72.5C-18351W |  |  | skip | no transformer I |  | 72.5 |  |  |  | I
E-M260026 | CM | CMIII-500Y/72.5C-16150 |  |  | skip | no transformer I |  | 72.5 |  |  | Y | III
E-M260027-028 | CM | 3xCMI-800/170C-14131W | CM2I-800/170D-14131W | CM2I-1200/170D-14131W ¦ SHZVI-1000/170D-14131W ¦ SHZVI-1200/170D-14131W | eligible |  | 634.5 | 170 | 1397 | 6 | Y | I
E-M260029 | CM |  |  |  | skip | no sold_type
E-M260030 | CM | 3xCMI-800/170B-14131W | CM2I-800/170D-14131W | CM2I-1200/170D-14131W ¦ SHZVI-1000/170D-14131W ¦ SHZVI-1200/170D-14131W | eligible |  | 678 | 170 | 1400 | 6 | Y | I
E-M260031 | CM | CMIII-500Y/72.5B-500 | CV2III-350Y/72.5-10193W | CV2III-600Y/72.5-10193W ¦ CVIII-350Y/72.5-10193W ¦ SVIII-500Y/72.5-10193W | eligible |  | 250 | 72.5 | 1123 |  | Y | III
E-M260032-033 | CM | 3xCMI-1200Y/170C-14131W | CM2I-1200/170D-14131W | CM2I-1500/170D-14131W ¦ SHZVI-1200/170D-14131W ¦ SHZVI-1500/170D-14131W | eligible |  | 1068 | 170 | 1328 | 6 | Y | I
E-M260034 | CM | CMIII-500Y/126B-10193W | CV2III-350Y/126-10193W | CV2III-600Y/126-10193W ¦ CM2III-500Y/126C-10193W ¦ CM2III-600Y/126C-10193W | eligible |  | 244.9 | 126 | 1368 | 8 | Y | III
E-M260035 | CM | CMIII-500Y/72.5B-10193W | CV2III-350Y/72.5-10193W | CV2III-600Y/72.5-10193W ¦ CVIII-350Y/72.5-10193W ¦ SVIII-500Y/72.5-10193W | eligible |  | 125 | 72.5 | 1368 | 8 | Y | III
E-M260036 | CM | CMIII-500Y/72.5B-10191W | CV2III-600Y/72.5-10191W | SVIII-500Y/72.5-10191W ¦ CM2III-500Y/72.5B-10191W ¦ CM2III-600Y/72.5B-10191W | eligible |  | 424.3 | 72.5 | 1181 | 9 | Y | III
E-M260037 | CM | CMIII-500Y/72.5B-14273W | CM2III-500Y/72.5B-14273W | CM2III-600Y/72.5B-14273W ¦ SHZVIII-400Y/72.5B-14273W ¦ SHZVIII-600Y/72.5B-14273W | eligible |  | 105.7 | 72.5 | 1328 | 12 | Y | III
E-M260038 | CM | CMIII-500Y/72.5B-14273W | CM2III-500Y/72.5B-14273W | CM2III-600Y/72.5B-14273W ¦ SHZVIII-400Y/72.5B-14273W ¦ SHZVIII-600Y/72.5B-14273W | eligible |  | 104.59 | 72.5 | 1328 | 12 | Y | III
E-M260039 | CM | 3xCMI-800/170C-14131W | CM2I-800/170D-14131W | CM2I-1200/170D-14131W ¦ SHZVI-1000/170D-14131W ¦ SHZVI-1200/170D-14131W | eligible |  | 634.5 | 170 | 1397 | 6 | Y | I
E-M260040-041 | CM | CMIII-500Y/72.5B-10193W | CV2III-350Y/72.5-10193W | CV2III-600Y/72.5-10193W ¦ CVIII-350Y/72.5-10193W ¦ SVIII-500Y/72.5-10193W | eligible |  | 97.2 | 72.5 | 1368.3 | 8 | Y | III
E-M260042 | CM |  |  |  | skip | no sold_type |  |  | 1368
E-M260044 | CM | CMIII-500Y/72.5B-14273W | CM2III-500Y/72.5B-14273W | CM2III-600Y/72.5B-14273W ¦ SHZVIII-400Y/72.5B-14273W ¦ SHZVIII-600Y/72.5B-14273W | eligible |  | 330.3 | 72.5 | 1328 | 12 | Y | III
E-M260045 | CM |  |  |  | skip | no sold_type | 668 |  | 2656 | 6
E-M260046 | CM |  |  |  | skip | no sold_type
E-M260047 | CM |  |  |  | skip | no sold_type
E-M260048-049 | CM | CMIII-500Y/72.5B-14273W | CM2III-500Y/72.5B-14273W | CM2III-600Y/72.5B-14273W ¦ SHZVIII-400Y/72.5B-14273W ¦ SHZVIII-600Y/72.5B-14273W | eligible |  | 106 | 72.5 | 1328 | 12 | Y | III
E-M260050-052 | CM | CMIII-500Y/72.5C-16150 |  |  | skip | no transformer I |  | 72.5 | 1298 |  | Y | III
E-M260053-072 | CM | CMIII-500Y/72.5C-16150 |  |  | skip | no transformer I |  | 72.5 | 1422 |  | Y | III
E-M260073-075 | CM | CMIII-500Y/72.5C-16150 |  |  | skip | no transformer I |  | 72.5 | 1422 |  | Y | III
E-M260076-081 | CM | CMIII-500Y/72.5C-16150 |  |  | skip | no transformer I |  | 72.5 | 1576 |  | Y | III
E-M260082-086 | CM | CMIII-500Y/72.5C-16150 |  |  | skip | no transformer I |  | 72.5 | 1576 |  | Y | III
E-M260087-088 | CM |  |  |  | skip | no sold_type
E-M260089-090 | CM |  |  |  | skip | no sold_type
E-M260091 | CM | CMIII-500Y/72.5C-16150 |  |  | skip | no transformer I |  | 72.5 |  |  | Y | III
E-M260092,E-M260094 | CM | CMI-500/170C-10193W | CM2I-500/170D-10193W | CM2I-600/170D-10193W ¦ SHZVI-400/170D-10193W ¦ SHZVI-600/170D-10193W | eligible |  | 316 | 170 | 1048 | 8 | Y | I
E-M260093 | CM | CMIII-600Y/72.5C-14271G | CVIII-350Y/72.5-14271G | CM2III-500Y/72.5B-14271G ¦ CM2III-600Y/72.5B-14271G ¦ SHZVIII-400Y/72.5B-14271G | eligible |  | 68.7 | 72.5 | 0 | 13 | Y | III
E-M260095-096 | CM | 3xCMI-1200/170B-14131W | CM2I-1200/170D-14131W | CM2I-1500/170D-14131W ¦ SHZVI-1200/170D-14131W ¦ SHZVI-1500/170D-14131W | eligible |  | 971.8 | 170 | 1852.9 | 6 | Y | I
E-M260097-098 | CM |  |  |  | skip | no sold_type
E-M260099-101 | CM | CMIII-500Y/126B-10193W | CV2III-350Y/126-10193W | CV2III-600Y/126-10193W ¦ CM2III-500Y/126C-10193W ¦ CM2III-600Y/126C-10193W | eligible |  | 244.9 | 126 | 1368 | 8 | Y | III
E-M260102 | CM | CMIII-500Y/126B-10091W | CV2III-350Y/126-10091W | CV2III-600Y/126-10091W ¦ CM2III-500Y/126C-10091W ¦ CM2III-600Y/126C-10091W | eligible |  | 100.41 | 126 | 1660 | 4 | Y | III
E-M260103 | CM | 3xCMI-1200/170B-14131W |  |  | skip | no transformer I |  | 170 |  |  |  | I
E-M260104-105 | CM | CMI-800/126-14131W |  |  | skip | no transformer I |  | 126 | 1397 | 6 |  | I
E-M260106-107 | CM |  |  |  | skip | no sold_type
E-M260108 | CM | 3xCMI-1200/170C-14131W |  |  | skip | no transformer I |  | 170 | 1328 | 6 |  | I
E-M260109 | CM | 3xCMI-1200/170B-14131W | CM2I-1200/170D-14131W | CM2I-1500/170D-14131W ¦ SHZVI-1200/170D-14131W ¦ SHZVI-1500/170D-14131W | eligible |  | 1084 | 170 | 1346 | 6 | Y | I
E-M260110 | CM | CMIII-500Y/126B-10193W |  |  | skip | no transformer I |  | 126 |  |  | Y | III
E-M260111 | CM | 3xCMI-1500/126B-14131W | CM2I-1500/126C-14131W | SHZVI-1500/126C-14131W ¦ SHZVI-1600/126C-14131W ¦ SHZVGI-3000/126C-14131W | eligible |  | 1296.6 | 126 | 1398 | 6 | Y | I
E-M260112 | CM | CMIII-500Y/72.5B-10191W |  |  | skip | no transformer I |  | 72.5 |  |  | Y | III
E-M260113 | CM | 3xCMI-1500/170C-14131W | CM2I-1500/170D-14131W | SHZVI-1500/170D-14131W ¦ SHZVI-1600/170D-14131W ¦ SHZVGI-3000/170D-14131W | eligible |  | 1269 | 170 | 0 | 6 | Y | I
E-M260114 | CM | 3xCMI-800/252B-14131W | CM2I-800/252D-14131W | CM2I-1200/252D-14131W ¦ SHZVI-1000/252D-14131W ¦ SHZVI-1200/252D-14131W | eligible |  | 667.6 | 252 | 2688.9 | 6 | Y | I
E-M260115 | CM | CMIII-600Y/72.5C-18531G |  |  | skip | no transformer I |  | 72.5 |  |  | Y | III
E-M260116-117 | CM | 3xCMI-1200/170B-14131W | CM2I-1200/170D-14131W | CM2I-1500/170D-14131W ¦ SHZVI-1200/170D-14131W ¦ SHZVI-1500/170D-14131W | eligible |  | 1068.2 | 170 | 1413.5 | 6 | Y | I
E-M260118-119 | CM | CMIII-500Y/72.5C-14273W | CM2III-500Y/72.5B-14273W | CM2III-600Y/72.5B-14273W ¦ SHZVIII-400Y/72.5B-14273W ¦ SHZVIII-600Y/72.5B-14273W | eligible |  | 106 | 72.5 | 1330 | 12 | Y | III
E-M260120-121 | CM | CMIII-500Y/72.5C-18170 | CM2III-500Y/72.5B-18170 | CM2III-600Y/72.5B-18170 ¦ SHZVIII-400Y/72.5B-18170 ¦ SHZVIII-600Y/72.5B-18170 | eligible |  | 141 | 72.5 | 1398 |  | Y | III
E-M260122 | CM | 3xCMI-1500Y/126B-14131W | CM2I-1500/126C-14131W | SHZVI-1500/126C-14131W ¦ SHZVI-1600/126C-14131W ¦ SHZVGI-3000/126C-14131W | eligible |  | 1269 | 126 | 1397 | 6 | Y | I
E-M260123 | CM | 3xCMI-1200/170B-14131W | CM2I-1200/170D-14131W | CM2I-1500/170D-14131W ¦ SHZVI-1200/170D-14131W ¦ SHZVI-1500/170D-14131W | eligible |  | 1068.2 | 170 | 1413.5 | 6 | Y | I
E-M260124-126 | CM | 3xCMI-1500/170C-14131W | CM2I-1500/170D-14131W | SHZVI-1500/170D-14131W ¦ SHZVI-1600/170D-14131W ¦ SHZVGI-3000/170D-14131W | eligible |  | 1356 | 170 | 1398 | 6 | Y | I
E-M260127-135 | CM | CMIII-500Y/72.5C-16150 |  |  | skip | no transformer I |  | 72.5 |  |  | Y | III
E-M260136-138 | CM | CMIII-500Y/72.5C-16150 |  |  | skip | no transformer I |  | 72.5 |  |  | Y | III
E-M260139 | CM | CMIII-500Y/72.5C-16150 |  |  | skip | no transformer I |  | 72.5 |  |  | Y | III
E-M260140 | CM | CMIII-500Y/72.5C-14273W | CM2III-500Y/72.5B-14273W | CM2III-600Y/72.5B-14273W ¦ SHZVIII-400Y/72.5B-14273W ¦ SHZVIII-600Y/72.5B-14273W | eligible |  | 264 | 72.5 | 1328 | 12 | Y | III
E-M260141-142 | CM | 3xCMI-1500Y/170C-14131W |  |  | skip | no transformer I |  | 170 |  | 6 | Y | I
E-M260143 | CM | CMIII-500Y/126DE-14273W | CM2III-500Y/126C-14273W | CM2III-600Y/126C-14273W ¦ SHZVIII-400Y/126C-14273W ¦ SHZVIII-600Y/126C-14273W | eligible |  | 231.6 | 126 | 1588 | 12 | Y | III
E-M260144 | CM | CMIII-500Y/72.5C-10193W | CM2III-500Y/72.5B-10193W | CM2III-600Y/72.5B-10193W ¦ SHZVIII-400Y/72.5B-10193W ¦ SHZVIII-600Y/72.5B-10193W | eligible |  | 232.7 | 72.5 | 2858 | 8 | Y | III
E-M260145-147 | CM | 3xCMI-800/170B-14131W | CM2I-800/170D-14131W | CM2I-1200/170D-14131W ¦ SHZVI-1000/170D-14131W ¦ SHZVI-1200/170D-14131W | eligible |  | 668 | 170 | 1328 | 6 | Y | I
E-M260148-150 | CM | CMIII-500Y/72.5C-16150 |  |  | skip | no transformer I |  | 72.5 |  |  | Y | III
E-M260151 | CM | CMIII-500Y/72.5-10193W | CV2III-600Y/72.5-10193W | SVIII-500Y/72.5-10193W ¦ CM2III-500Y/72.5B-10193W ¦ CM2III-600Y/72.5B-10193W | eligible |  | 368 | 72.5 | 794 | 8 | Y | III
E-M260152-161 | CM | CMIII-500Y/72.5C-16150 |  |  | skip | no transformer I |  | 72.5 | 1576 |  | Y | III
E-M260162 | CM | CMI-1200/72.5C-18351W |  |  | skip | no transformer I |  | 72.5 |  |  |  | I
E-M260163 | CM | 3xCMI-1200/170B-14131W | CM2I-1200/170D-14131W | CM2I-1500/170D-14131W ¦ SHZVI-1200/170D-14131W ¦ SHZVI-1500/170D-14131W | eligible |  | 1068.2 | 170 | 1413.5 | 6 | Y | I
E-M260164 | CM | CMIII-500Y/72.5C-16150 |  |  | skip | no transformer I |  | 72.5 |  |  | Y | III
E-M260165 | CM |  |  |  | skip | no sold_type | 1068.2 |  | 1328 | 6
E-M260166 | CM |  |  |  | skip | no sold_type | 1068.2 |  | 1328 | 6
E-M260167-168 | CM | CMIII-600Y/72.5B-10173G | CV2III-600Y/72.5-16151G | CM2III-600Y/72.5B-16151G ¦ SHZVIII-600Y/72.5B-16151G ¦ SHZVIII-1000Y/72.5B-16151G | eligible |  | 575.2 | 72.5 | 238.2 | 7 | Y | III
E-CMD260001 | CMD | CMDIII-1000Y/72.5C-10193W | SHZVGIII-1300Y/72.5B-10193W | SHZVGIII-1500Y/72.5B-10193W ¦ 3xCM2I-1200/72.5B-10193W ¦ 3xCM2I-1500/72.5B-10193W | miss |  | 983 | 72.5 | 1417 | 8 | Y | III | I=983, oil CMD-1000; engine prefers vacuum SHZVG-1300 (CMD III 1000 not in vacuum rank)
E-CMD260004-005 | CMD | CMDI-1600/252C-14130 | SHZVI-1600/252D-14130 | SHZVI-2400/252D-14130 ¦ SHZVGI-3000/252D-14130 ¦ CMDI-1600/252D-14130 | eligible |  | 1322 | 252 | 2656 |  | Y | I
E-CMD260006 | CMD | CMDIII-1000Y/72.5B-10193W | SHZVIII-1000Y/72.5B-10193W | SHZVGIII-1300Y/72.5B-10193W ¦ SHZVGIII-1500Y/72.5B-10193W ¦ CMDIII-1000Y/72.5B-10193W | eligible |  | 668.4 | 72.5 | 377 | 8 | Y | III
E-CMD260007 | CMD | CMDIII-1000Y/72.5B-10193W | SHZVIII-1000Y/72.5B-10193W | SHZVGIII-1300Y/72.5B-10193W ¦ SHZVGIII-1500Y/72.5B-10193W ¦ CMDIII-1000Y/72.5B-10193W | eligible |  | 924 | 72.5 | 91 | 8 | Y | III
E-CMD260008 | CMD | CMDI-1600/252C-14130 | SHZVI-1600/252D-14130 | SHZVI-2400/252D-14130 ¦ SHZVGI-3000/252D-14130 ¦ CMDI-1600/252D-14130 | eligible |  | 1321.4 | 252 | 2683 |  | Y | I
E-CMD260009-010 | CMD | CMDI-1600/252C-14130 | CM2I-1500/252D-14130 | SHZVI-1500/252D-14130 ¦ SHZVI-1600/252D-14130 ¦ SHZVGI-3000/252D-14130 | eligible |  | 1321.4 | 252 | 0 |  | Y | I
E-CMD260011-013 | CMD | CMDI-1600/252C-14130 | CM2I-1500/252D-14130 | SHZVI-1500/252D-14130 ¦ SHZVI-1600/252D-14130 ¦ SHZVGI-3000/252D-14130 | eligible |  | 1321.4 | 252 | 0 |  | Y | I
E-CMD260014-015 | CMD |  |  |  | skip | no sold_type
E-V260001-002 | CV |  |  |  | skip | no sold_type
E-V260003 | CV | CVIII-350D/40.5-12233G | CV2III-350D/40.5-12233G | CV2III-600D/40.5-12233G ¦ CVIII-350D/40.5-12233G ¦ SVIII-500D/40.5-12233G | eligible |  | 266.62 | 40.5 | 346.5 | 10 | D | III
E-V260004-005 | CV | CVIII-350D/40.5-10193W | CV2III-350D/40.5-10193W | CV2III-600D/40.5-10193W ¦ CVIII-350D/40.5-10193W ¦ SVIII-500D/40.5-10193W | eligible |  | 227 | 40.5 | 257 | 8 | D | III
E-V260006-010 | CV |  |  |  | skip | no sold_type | 350
E-V260011 | CV |  |  |  | skip | no sold_type
E-V260012 | CV | SVIII-500Y/40.5-10193W | CV2III-600Y/40.5-10193W | SVIII-500Y/40.5-10193W ¦ CM2III-500Y/72.5B-10193W ¦ CM2III-600Y/72.5B-10193W | eligible |  | 386 | 40.5 | 275 | 8 | Y | III
E-V260013-014 | CV |  |  |  | skip | no sold_type
E-V260015 | CV | CVIII-350D/40.5-10193W | CV2III-350D/40.5-10193W | CV2III-600D/40.5-10193W ¦ CVIII-350D/40.5-10193W ¦ SVIII-500D/40.5-10193W | eligible |  | 103 | 40.5 | 144.3 | 8 | D | III
E-V260016-017 | CV |  |  |  | skip | no sold_type
E-V260018-019 | CV | CVIII-350Y/72.5-10191W |  |  | skip | no transformer I |  | 72.5 |  |  | Y | III
E-V260020-021 | CV | CVIII-350D/40.5-10193G |  |  | skip | no transformer I |  | 40.5 |  |  | D | III
E-V260022 | CV | CVIII-350D/40.5-10131G | CV2III-350D/40.5-10153G | CV2III-600D/40.5-10153G ¦ CVIII-350D/40.5-10153G ¦ SVIII-500D/40.5-10153G | eligible |  | 43.9 | 40.5 | 306 | 6 | D | III
E-V260023-024 | CV | CVIII-350Y/72.5-10191W | CV2III-350Y/72.5-10191W | CV2III-600Y/72.5-10191W ¦ CVIII-350Y/72.5-10191W ¦ SVIII-500Y/72.5-10191W | eligible |  | 212.1 | 72.5 | 1182 | 9 | Y | III
E-V260025-026 | CV | CVIII-350/12-233 |  |  | skip | no transformer I |  | 12 |  | 10 |  | III
E-V260027-028 | CV | SVIII-500Y/72.5-10193W | CV2III-600Y/72.5-10193W | SVIII-500Y/72.5-10193W ¦ CM2III-500Y/72.5B-10193W ¦ CM2III-600Y/72.5B-10193W | eligible |  | 418 | 72.5 | 318 | 8 | Y | III
E-V260029 | CV | CVIII-350D/40.5-10193W | CV2III-350D/40.5-10193W | CV2III-600D/40.5-10193W ¦ CVIII-350D/40.5-10193W ¦ SVIII-500D/40.5-10193W | eligible |  | 114 | 40.5 | 345 | 8 | D | III
E-V260030 | CV | CVIII-350D/40.5-10193W | CV2III-350D/40.5-10193W | CV2III-600D/40.5-10193W ¦ CVIII-350D/40.5-10193W ¦ SVIII-500D/40.5-10193W | eligible |  | 196.1 | 40.5 | 216.65 | 8 | D | III
E-V260031-033 | CV | CVIII-350D/40.5-14131W | CV2III-350D/40.5-14131W | CV2III-600D/40.5-14131W ¦ CVIII-350D/40.5-14131W ¦ SVIII-500D/40.5-14131W | eligible |  | 222.2 | 40.5 | 498.5 | 6 | D | III
E-V260034-035 | CV |  |  |  | skip | no sold_type
E-V260036-038 | CV | SVIII-500D/40.5-10193W | CV2III-600D/40.5-10193W | SVIII-500D/40.5-10193W ¦ CM2III-500D/72.5B-10193W ¦ CM2III-600D/72.5B-10193W | eligible |  | 412.39 | 40.5 | 216.51 | 8 | D | III
E-V260039 | CV |  |  |  | skip | no sold_type
E-V260040-041 | CV | CVIII-350D/40.5-10193W | CV2III-350D/40.5-10193W | CV2III-600D/40.5-10193W ¦ CVIII-350D/40.5-10193W ¦ SVIII-500D/40.5-10193W | eligible |  | 206.2 | 40.5 | 216.51 | 8 | D | III
E-V260042 | CV | CVIII-350D/40.5-10191W | CV2III-350D/40.5-10191W | CV2III-600D/40.5-10191W ¦ CVIII-350D/40.5-10191W ¦ SVIII-500D/40.5-10191W | eligible |  | 80.6 | 40.5 | 165 | 9 | D | III
E-V260043-044 | CV | SVIII-500Y/40.5-10193W | CV2III-600Y/40.5-10193W | SVIII-500Y/40.5-10193W ¦ CM2III-500Y/72.5B-10193W ¦ CM2III-600Y/72.5B-10193W | eligible |  | 417.8 | 40.5 | 551 | 8 | Y | III
E-V260045-047 | CV | CVIII-350D/40.5-10090 | CV2III-350D/40.5-10090 | CV2III-600D/40.5-10090 ¦ CVIII-350D/40.5-10090 ¦ SVIII-500D/40.5-10090 | eligible |  | 178.3 | 40.5 | 825 |  | D | III
E-V260048 | CV | CVIII-350D/72.5-10193W | CV2III-350D/72.5-10193W | CV2III-600D/72.5-10193W ¦ CVIII-350D/72.5-10193W ¦ SVIII-500D/72.5-10193W | eligible |  | 80.5 | 72.5 | 862.5 | 8 | D | III
E-V260049 | CV | CVIII-350Y/72.5-10191W |  |  | skip | no transformer I |  | 72.5 |  |  | Y | III
E-V260050 | CV | CVIII-350D/40.5-12233W | CV2III-350D/40.5-12233W | CV2III-600D/40.5-12233W ¦ CVIII-350D/40.5-12233W ¦ SVIII-500D/40.5-12233W | eligible |  | 222.22 | 40.5 | 500 | 10 | D | III
E-V260051-052 | CV |  |  |  | skip | no sold_type
E-V260053 | CV | CVIII-350Y/72.5-10191W |  |  | skip | no transformer I |  | 72.5 |  |  | Y | III
E-V260054-063 | CV |  |  |  | skip | no sold_type | 350
E-V260064-065 | CV |  |  |  | skip | no sold_type
E-V260066-067 | CV |  |  |  | skip | no sold_type
E-V260068-069 | CV |  |  |  | skip | no sold_type
E-V260070 | CV |  |  |  | skip | no sold_type
E-V260070 | CV |  |  |  | skip | no sold_type
E-V260071 | CV | CVIII-350D/72.5-10193W | CV2III-350D/72.5-10193W | CV2III-600D/72.5-10193W ¦ CVIII-350D/72.5-10193W ¦ SVIII-500D/72.5-10193W | eligible |  | 52.3 | 72.5 | 862 | 8 | D | III
E-V260072 | CV |  |  |  | skip | no sold_type
E-V260073 | CV | CVIII-350Y/72.5-10191W | CV2III-350Y/72.5-10191W | CV2III-600Y/72.5-10191W ¦ CVIII-350Y/72.5-10191W ¦ SVIII-500Y/72.5-10191W | eligible |  | 212 | 72.5 | 1182 | 9 | Y | III
E-V260074-075 | CV | CVIII-350D/40.5-10193G | CV2III-350D/40.5-10193G | CV2III-600D/40.5-10193G ¦ CVIII-350D/40.5-10193G ¦ SVIII-500D/40.5-10193G | eligible |  | 50.3 | 40.5 | 412.5 | 8 | D | III
E-V260076 | CV |  |  |  | skip | no sold_type
E-V260077 | CV |  |  |  | skip | no sold_type
E-V260078 | CV | CVIII-350/12-233 |  |  | skip | no transformer I |  | 12 |  | 10 |  | III
E-V260079-080 | CV |  |  |  | skip | no sold_type
E-V260081-082 | CV |  |  |  | skip | no sold_type
E-V260083 | CV |  |  |  | skip | no sold_type
E-V260084 | CV | CVIII-350Y/72.5-10191W | CV2III-350Y/72.5-10191W | CV2III-600Y/72.5-10191W ¦ CVIII-350Y/72.5-10191W ¦ SVIII-500Y/72.5-10191W | eligible |  | 334 | 72.5 | 1182 | 9 | Y | III
E-V260085 | CV | CVIII-350Y/72.5-10191W | CV2III-350Y/72.5-10191W | CV2III-600Y/72.5-10191W ¦ CVIII-350Y/72.5-10191W ¦ SVIII-500Y/72.5-10191W | eligible |  | 212 | 72.5 | 1182 | 9 | Y | III
E-V260086 | CV | CVIII-350Y/72.5-10191W | CV2III-350Y/72.5-10191W | CV2III-600Y/72.5-10191W ¦ CVIII-350Y/72.5-10191W ¦ SVIII-500Y/72.5-10191W | eligible |  | 133 | 72.5 | 1182 | 9 | Y | III
E-V260087-088 | CV |  |  |  | skip | no sold_type |  |  |  | 9
E-V260089 | CV |  |  |  | skip | no sold_type
E-V260090 | CV | CVIII-350D/72.5-10193W | CV2III-350D/72.5-10193W | CV2III-600D/72.5-10193W ¦ CVIII-350D/72.5-10193W ¦ SVIII-500D/72.5-10193W | eligible |  | 80.5 | 72.5 | 862.5 | 8 | D | III
E-V260091-092 | CV |  |  |  | skip | no sold_type
E-V260093-094 | CV | CVIII-350D/72.5-10193W | CV2III-350D/72.5-10193W | CV2III-600D/72.5-10193W ¦ CVIII-350D/72.5-10193W ¦ SVIII-500D/72.5-10193W | eligible |  | 230 | 72.5 | 578 | 8 | D | III
E-V260095-096 | CV |  |  |  | skip | no sold_type
E-V260097 | CV | CVIII-350Y/72.5-10191W | CV2III-350Y/72.5-10191W | CV2III-600Y/72.5-10191W ¦ CVIII-350Y/72.5-10191W ¦ SVIII-500Y/72.5-10191W | eligible |  | 84.9 | 72.5 | 1182 | 9 | Y | III
E-V260098-099 | CV | CVIII-350D/72.5-10193G |  |  | skip | no transformer I |  | 72.5 |  |  | D | III
E-V260100 | CV | CVIII-350Y/40.5-10193W | CV2III-350Y/40.5-10193W | CV2III-600Y/40.5-10193W ¦ CVIII-350Y/40.5-10193W ¦ SVIII-500Y/40.5-10193W | eligible |  | 218.7 | 40.5 | 158.77 | 8 | Y | III
E-V260101 | CV |  |  |  | skip | no sold_type
E-V260102-103 | CV | CVIII-350Y/72.5-10193W | CV2III-350Y/72.5-10193W | CV2III-600Y/72.5-10193W ¦ CVIII-350Y/72.5-10193W ¦ SVIII-500Y/72.5-10193W | eligible |  | 281 | 72.5 | 0 | 8 | Y | III
E-V260104 | CV | CVIII-350D/72.5-14131W | CV2III-350D/72.5-14131W | CV2III-600D/72.5-14131W ¦ CVIII-350D/72.5-14131W ¦ SVIII-500D/72.5-14131W | eligible |  | 67.09 | 72.5 | 862.5 | 6 | D | III
E-V260105-106 | CV | CVIII-350D/72.5-10173G | CV2III-350D/72.5-16151G | CV2III-600D/72.5-16151G ¦ CVIII-350D/72.5-16151G ¦ SVIII-500D/72.5-16151G | eligible |  | 71.6 | 72.5 | 693 | 7 | D | III
E-V260107 | CV | CVIII-350Y/72.5-10173G | CV2III-350Y/72.5-16151G | CV2III-600Y/72.5-16151G ¦ CVIII-350Y/72.5-16151G ¦ SVIII-500Y/72.5-16151G | eligible |  | 62.1 | 72.5 | 400.1 | 7 | Y | III
E-V260108-109 | CV | CVIII-350Y/72.5-10173G | CV2III-350Y/72.5-16151G | CV2III-600Y/72.5-16151G ¦ CVIII-350Y/72.5-16151G ¦ SVIII-500Y/72.5-16151G | eligible |  | 99.3 | 72.5 | 400.1 | 7 | Y | III
E-V260110-113 | CV | CVIII-350D/40.5-12231G | CV2III-350D/40.5-12231G | CV2III-600D/40.5-12231G ¦ CVIII-350D/40.5-12231G ¦ SVIII-500D/40.5-12231G | eligible |  | 59.4 | 40.5 | 472.5 | 11 | D | III
E-V260114-116 | CV | CVIII-350Y/40.5-12231G | CV2III-350Y/40.5-12231G | CV2III-600Y/40.5-12231G ¦ CVIII-350Y/40.5-12231G ¦ SVIII-500Y/40.5-12231G | eligible |  | 109.8 | 40.5 | 272.8 | 11 | Y | III
E-V260117 | CV | CVIII-350Y/40.5-12231G | CV2III-350Y/40.5-12231G | CV2III-600Y/40.5-12231G ¦ CVIII-350Y/40.5-12231G ¦ SVIII-500Y/40.5-12231G | eligible |  | 219.5 | 40.5 | 272.8 | 11 | Y | III
E-V260118 | CV | 3xCVIII-350Y/72.5-10193W | CV2III-350Y/72.5-10193W | CV2III-600Y/72.5-10193W ¦ CVIII-350Y/72.5-10193W ¦ SVIII-500Y/72.5-10193W | oil-vs-vac |  | 87.5 | 72.5 | 1134.5 | 8 | Y | III
E-V260119 | CV | CVIII-350Y/72.5-10191W |  |  | skip | no transformer I |  | 72.5 |  |  | Y | III
E-V260120-121 | CV | CVIII-350Y/72.5-10191W |  |  | skip | no transformer I |  | 72.5 |  |  | Y | III
E-V260124-125 | CV |  |  |  | skip | no sold_type
E-V260126-127 | CV |  |  |  | skip | no sold_type | 239 |  | 1181.8 | 9
E-V260128-129 | CV |  |  |  | skip | no sold_type
E-V260130-131 | CV | CVIII-350Y/72.5-10191W | CV2III-350Y/72.5-10191W | CV2III-600Y/72.5-10191W ¦ CVIII-350Y/72.5-10191W ¦ SVIII-500Y/72.5-10191W | eligible |  | 212 | 72.5 | 1182 | 9 | Y | III
E-V260132-133 | CV | CVIII-350D/40.5-10193G | CV2III-350D/40.5-10193G | CV2III-600D/40.5-10193G ¦ CVIII-350D/40.5-10193G ¦ SVIII-500D/40.5-10193G | eligible |  | 227.3 | 40.5 | 431.2 | 8 | D | III
E-V260134-135 | CV | CVIII-350Y/72.5-10193W | CV2III-350Y/72.5-10193W | CV2III-600Y/72.5-10193W ¦ CVIII-350Y/72.5-10193W ¦ SVIII-500Y/72.5-10193W | eligible |  | 176 | 72.5 | 303 | 8 | Y | III
E-V260136-137 | CV | CVIII-350Y/72.5-10191W | CV2III-350Y/72.5-10191W | CV2III-600Y/72.5-10191W ¦ CVIII-350Y/72.5-10191W ¦ SVIII-500Y/72.5-10191W | eligible |  | 334 | 72.5 | 1182 | 9 | Y | III
E-V260138-139 | CV |  |  |  | skip | no sold_type
E-V260140 | CV | CVIII-350Y/72.5-10191W | CV2III-350Y/72.5-10191W | CV2III-600Y/72.5-10191W ¦ CVIII-350Y/72.5-10191W ¦ SVIII-500Y/72.5-10191W | eligible |  | 133 | 72.5 | 1182 | 9 | Y | III
E-V260141 | CV | CVI-700Y/72.5-10070 | CV2I-350/72.5-10070 | CV2I-600/72.5-10070 ¦ CVI-350/72.5-10070 ¦ CVI-700/72.5-10070 | eligible |  | 269.27 | 72.5 | 769.5 |  | Y | I
E-V260143 | CV |  |  |  | skip | no sold_type
E-V260144 | CV |  |  |  | skip | no sold_type | 148.15 |  | 250
E-V260145 | CV | CVIII-350Y/72.5-10191W | CV2III-350Y/72.5-10191W | CV2III-600Y/72.5-10191W ¦ CVIII-350Y/72.5-10191W ¦ SVIII-500Y/72.5-10191W | eligible |  | 133 | 72.5 | 1182 | 9 | Y | III
E-V260146-147 | CV | CVIII-350Y/72.5-10191W | CV2III-350Y/72.5-10191W | CV2III-600Y/72.5-10191W ¦ CVIII-350Y/72.5-10191W ¦ SVIII-500Y/72.5-10191W | eligible |  | 212 | 72.5 | 1182 | 9 | Y | III
E-V260148-149 | CV | CVIII-350Y/72.5-10191W | CV2III-350Y/72.5-10191W | CV2III-600Y/72.5-10191W ¦ CVIII-350Y/72.5-10191W ¦ SVIII-500Y/72.5-10191W | eligible |  | 334 | 72.5 | 1182 | 9 | Y | III
E-V260150 | CV | CVIII-350D/40.5-10090 | CV2III-350D/40.5-10090 | CV2III-600D/40.5-10090 ¦ CVIII-350D/40.5-10090 ¦ SVIII-500D/40.5-10090 | eligible |  | 178.3 | 40.5 | 825 |  | D | III
E-V260151 | CV | SVIII-500D/40.5-10193W |  |  | skip | no transformer I |  | 40.5 |  |  | D | III
E-V260152 | CV | CVIII-350D/40.5-1 |  |  | skip | no transformer I |  | 40.5 |  |  | D | III
E-V260153-154 | CV |  |  |  | skip | no sold_type
E-V260155 | CV | CVIII-350Y/72.5-10191W | CV2III-350Y/72.5-10191W | CV2III-600Y/72.5-10191W ¦ CVIII-350Y/72.5-10191W ¦ SVIII-500Y/72.5-10191W | eligible |  | 80 | 72.5 | 1182 | 9 | Y | III
E-V260156-157 | CV | CVIII-350Y/72.5-10191W | CV2III-350Y/72.5-10191W | CV2III-600Y/72.5-10191W ¦ CVIII-350Y/72.5-10191W ¦ SVIII-500Y/72.5-10191W | eligible |  | 334 | 72.5 | 1182 | 9 | Y | III
E-V260158-159 | CV | CVIII-350Y/72.5-10191W | CV2III-350Y/72.5-10191W | CV2III-600Y/72.5-10191W ¦ CVIII-350Y/72.5-10191W ¦ SVIII-500Y/72.5-10191W | eligible |  | 21.2 | 72.5 | 1182 | 9 | Y | III
E-V260160-161 | CV | CVIII-350Y/72.5-10193W | CV2III-350Y/72.5-10193W | CV2III-600Y/72.5-10193W ¦ CVIII-350Y/72.5-10193W ¦ SVIII-500Y/72.5-10193W | eligible |  | 267 | 72.5 | 318 | 8 | Y | III
E-V260162 | CV |  |  |  | skip | no sold_type
E-V260163-164 | CV | CVIII-350D/40.5-10193W |  |  | skip | no transformer I |  | 40.5 |  |  | D | III
E-V260165 | CV |  |  |  | skip | no sold_type
E-V260166 | CV | CVIII-350D/40.5-10193W |  |  | skip | no transformer I |  | 40.5 |  |  | D | III
E-V260167-168 | CV | CVIII-350D/40.5-14271W |  |  | skip | no transformer I |  | 40.5 |  |  | D | III
E-V260169 | CV | CVIII-350Y/40.5-10193W | CV2III-350Y/40.5-10193W | CV2III-600Y/40.5-10193W ¦ CVIII-350Y/40.5-10193W ¦ SVIII-500Y/40.5-10193W | eligible |  | 267 | 40.5 | 318 | 8 | Y | III
E-V260170-178 | CV |  |  |  | skip | no sold_type | 320
E-V260179 | CV |  |  |  | skip | no sold_type
E-V260180 | CV | CVIII-350Y/72.5-10090 | CV2III-350Y/72.5-10090 | CV2III-600Y/72.5-10090 ¦ CVIII-350Y/72.5-10090 ¦ SVIII-500Y/72.5-10090 | eligible |  | 114.2 | 72.5 | 454.7 |  | Y | III
E-V260181 | CV | CVIII-350Y/72.5-10193W | CV2III-350Y/72.5-10193W | CV2III-600Y/72.5-10193W ¦ CVIII-350Y/72.5-10193W ¦ SVIII-500Y/72.5-10193W | eligible |  | 167 | 72.5 | 318 | 8 | Y | III
E-V260182 | CV | CVIII-350Y/72.5-10191W | CV2III-350Y/72.5-10191W | CV2III-600Y/72.5-10191W ¦ CVIII-350Y/72.5-10191W ¦ SVIII-500Y/72.5-10191W | eligible |  | 53 | 72.5 | 1182 | 9 | Y | III
E-V260183-184 | CV | CVIII-350Y/40.5-10193W | CV2III-350Y/40.5-10193W | CV2III-600Y/40.5-10193W ¦ CVIII-350Y/40.5-10193W ¦ SVIII-500Y/40.5-10193W | eligible |  | 267 | 40.5 | 318 | 8 | Y | III
E-V260185 | CV | CVIII-350Y/40.5-10193W | CV2III-350Y/40.5-10193W | CV2III-600Y/40.5-10193W ¦ CVIII-350Y/40.5-10193W ¦ SVIII-500Y/40.5-10193W | eligible |  | 267 | 40.5 | 318 | 8 | Y | III
E-V260186-187 | CV | CVIII-350Y/72.5-10191W | CV2III-350Y/72.5-10191W | CV2III-600Y/72.5-10191W ¦ CVIII-350Y/72.5-10191W ¦ SVIII-500Y/72.5-10191W | eligible |  | 212 | 72.5 | 1182 | 9 | Y | III
E-V260188-197 | CV |  |  |  | skip | no sold_type
E-V260198-199 | CV | CVIII-350Y/72.5-10191W | CV2III-350Y/72.5-10191W | CV2III-600Y/72.5-10191W ¦ CVIII-350Y/72.5-10191W ¦ SVIII-500Y/72.5-10191W | eligible |  | 53 | 72.5 | 1182 | 9 | Y | III
E-V260200-202 | CV |  |  |  | skip | no sold_type
E-V260203 | CV | CVIII-350Y/72.5-10191W | CV2III-350Y/72.5-10191W | CV2III-600Y/72.5-10191W ¦ CVIII-350Y/72.5-10191W ¦ SVIII-500Y/72.5-10191W | eligible |  | 149.45 | 72.5 | 1181.84 | 9 | Y | III
E-V260204 | CV | CVIII-350Y/40.5-12111W |  |  | skip | no transformer I |  | 40.5 |  |  | Y | III
E-V260205-206 | CV | CVIII-350D/72.5-10193W | CV2III-350D/72.5-10193W | CV2III-600D/72.5-10193W ¦ CVIII-350D/72.5-10193W ¦ SVIII-500D/72.5-10193W | eligible |  | 50.3 | 72.5 | 862.5 | 8 | D | III
E-V260207-208 | CV | CVIII-350Y/72.5-10193W | CV2III-350Y/72.5-10193W | CV2III-600Y/72.5-10193W ¦ CVIII-350Y/72.5-10193W ¦ SVIII-500Y/72.5-10193W | eligible |  | 167 | 72.5 | 318 | 8 | Y | III
E-V260209 | CV | CVIII-350Y/72.5-10191W | CV2III-350Y/72.5-10191W | CV2III-600Y/72.5-10191W ¦ CVIII-350Y/72.5-10191W ¦ SVIII-500Y/72.5-10191W | eligible |  | 132.6 | 72.5 | 1180 | 9 | Y | III
E-V260210-211 | CV | CVIII-350Y/72.5-10191W | CV2III-350Y/72.5-10191W | CV2III-600Y/72.5-10191W ¦ CVIII-350Y/72.5-10191W ¦ SVIII-500Y/72.5-10191W | eligible |  | 133 | 72.5 | 1182 | 9 | Y | III
E-V260212-214 | CV |  |  |  | skip | no sold_type
E-V260215-216 | CV | CVIII-350D/40.5-10193W | CV2III-350D/40.5-10193W | CV2III-600D/40.5-10193W ¦ CVIII-350D/40.5-10193W ¦ SVIII-500D/40.5-10193W | eligible |  | 333.09 | 40.5 | 500 | 8 | D | III
E-V260217-218 | CV |  |  |  | skip | no sold_type
E-V260219 | CV |  |  |  | skip | no sold_type
E-V260220 | CV |  |  |  | skip | no sold_type
E-V260221-222 | CV | SVIII-500Y/72.5-10193W | CV2III-600Y/72.5-10193W | SVIII-500Y/72.5-10193W ¦ CM2III-500Y/72.5B-10193W ¦ CM2III-600Y/72.5B-10193W | eligible |  | 446.7 | 72.5 | 0 | 8 | Y | III
E-V260223 | CV | CVIII-350Y/72.5-10191W | CV2III-350Y/72.5-10191W | CV2III-600Y/72.5-10191W ¦ CVIII-350Y/72.5-10191W ¦ SVIII-500Y/72.5-10191W | eligible |  | 334 | 72.5 | 1209 | 9 | Y | III
E-V260224-229 | CV |  |  |  | skip | no sold_type
E-V260230-231 | CV |  |  |  | skip | no sold_type
E-V260232 | CV |  |  |  | skip | no sold_type
E-V260233 | CV |  |  |  | skip | no sold_type
E-V260234 | CV | CVIII-350Y/72.5-10193W |  |  | skip | no transformer I |  | 72.5 | 318 | 8 | Y | III
E-V260235-236 | CV | CVIII-350Y/72.5-10191W | CV2III-350Y/72.5-10191W | CV2III-600Y/72.5-10191W ¦ CVIII-350Y/72.5-10191W ¦ SVIII-500Y/72.5-10191W | eligible |  | 212 | 72.5 | 1182 | 9 | Y | III
E-V260237-238 | CV | CVIII-350Y/72.5-10191W | CV2III-350Y/72.5-10191W | CV2III-600Y/72.5-10191W ¦ CVIII-350Y/72.5-10191W ¦ SVIII-500Y/72.5-10191W | eligible |  | 133 | 72.5 | 1187 | 9 | Y | III
E-V260239 | CV | CVIII-350D/40.5-1 |  |  | skip | no transformer I |  | 40.5 |  |  | D | III
E-V260240 | CV | CVIII-350D/40.5-1 |  |  | skip | no transformer I |  | 40.5 |  |  | D | III
E-V260241 | CV | CVIII-350Y/72.5-10191W | CV2III-350Y/72.5-10191W | CV2III-600Y/72.5-10191W ¦ CVIII-350Y/72.5-10191W ¦ SVIII-500Y/72.5-10191W | eligible |  | 334 | 72.5 | 1182 | 9 | Y | III
E-V260242-244 | CV | CVIII-350D/40.5-14131W | CV2III-350D/40.5-14131W | CV2III-600D/40.5-14131W ¦ CVIII-350D/40.5-14131W ¦ SVIII-500D/40.5-14131W | eligible |  | 138.8 | 40.5 | 498.5 | 6 | D | III
E-V260245-248 | CV | CVIII-350Y/72.5-12233W | CV2III-350Y/72.5-12233W | CV2III-600Y/72.5-12233W ¦ CVIII-350Y/72.5-12233W ¦ SVIII-500Y/72.5-12233W | eligible |  | 267.3 | 72.5 | 433 | 10 | Y | III
E-V260249-250 | CV |  |  |  | skip | no sold_type
E-V260251-252 | CV |  |  |  | skip | no sold_type
E-V260253-256 | CV |  |  |  | skip | no sold_type
E-V260257-260 | CV |  |  |  | skip | no sold_type
E-V260261-268 | CV |  |  |  | skip | no sold_type
E-V260269 | CV | CVIII-350D/40.5-14271W | CVIII-350D/40.5-14271W | CM2III-500D/72.5B-14271W ¦ CM2III-600D/72.5B-14271W ¦ SHZVIII-400D/72.5B-14271W | exact |  | 197.95 | 40.5 | 202 | 13 | D | III
E-V260270 | CV | CVIII-350D/40.5-10090 |  |  | skip | no transformer I |  | 40.5 |  |  | D | III
E-V260271 | CV | CVIII-350D/72.5-14271G | CVIII-350D/72.5-14271G | CM2III-500D/72.5B-14271G ¦ CM2III-600D/72.5B-14271G ¦ SHZVIII-400D/72.5B-14271G | exact |  | 250 | 72.5 | 475 | 13 | D | III
E-V260272 | CV | CVIII-350Y/72.5-10191W |  |  | skip | no transformer I |  | 72.5 |  |  | Y | III
E-V260273-275 | CV | CVIII-350Y/72.5-10191W |  |  | skip | no transformer I |  | 72.5 |  |  | Y | III
E-V260276-277 | CV |  |  |  | skip | no sold_type
E-V260278 | CV | CVIII-350Y/72.5-10193W | CV2III-350Y/72.5-10193W | CV2III-600Y/72.5-10193W ¦ CVIII-350Y/72.5-10193W ¦ SVIII-500Y/72.5-10193W | eligible |  | 176 | 72.5 | 303 | 8 | Y | III
E-V260279 | CV | CVIII-350Y/72.5-10191W | CV2III-350Y/72.5-10191W | CV2III-600Y/72.5-10191W ¦ CVIII-350Y/72.5-10191W ¦ SVIII-500Y/72.5-10191W | eligible |  | 53 | 72.5 | 1182 | 9 | Y | III
E-V260280-281 | CV |  |  |  | skip | no sold_type |  |  |  | 9
E-V260282 | CV | SVIII-500Y/40.5-10193W | CV2III-600Y/40.5-10193W | SVIII-500Y/40.5-10193W ¦ CM2III-500Y/72.5B-10193W ¦ CM2III-600Y/72.5B-10193W | eligible |  | 417.8 | 40.5 | 417.8 | 8 | Y | III
E-V260283-285 | CV |  |  |  | skip | no sold_type
E-V260286-289 | CV | CVIII-350Y/72.5-10193W | CV2III-350Y/72.5-10193W | CV2III-600Y/72.5-10193W ¦ CVIII-350Y/72.5-10193W ¦ SVIII-500Y/72.5-10193W | eligible |  | 267 | 72.5 | 318 | 8 | Y | III
E-V260290 | CV | CVIII-350Y/40.5-12111W | CV2III-350Y/40.5-12111W | CV2III-600Y/40.5-12111W ¦ CVIII-350Y/40.5-12111W ¦ SVIII-500Y/40.5-12111W | eligible |  | 223.9 | 40.5 | 158.77 | 5 | Y | III
E-V260291 | CV | SVIII-500D/40.5-12231W | CV2III-600D/40.5-12231W | SVIII-500D/40.5-12231W ¦ CM2III-500D/72.5B-12231W ¦ CM2III-600D/72.5B-12231W | eligible |  | 400 | 40.5 | 260 | 11 | D | III
E-V260292 | CV | CVIII-350Y/72.5-10191W | CV2III-350Y/72.5-10191W | CV2III-600Y/72.5-10191W ¦ CVIII-350Y/72.5-10191W ¦ SVIII-500Y/72.5-10191W | eligible |  | 133 | 72.5 | 1182 | 9 | Y | III
E-V260293 | CV | CVI-350/40.5-10100W |  |  | skip | no transformer I |  | 40.5 |  |  |  | I
E-V260294 | CV | CVIII-350D/40.5-10090 | CV2III-350D/40.5-10090 | CV2III-600D/40.5-10090 ¦ CVIII-350D/40.5-10090 ¦ SVIII-500D/40.5-10090 | eligible |  | 11.2 | 40.5 | 825 |  | D | III
E-V260296 | CV | CVIII-350Y/72.5-10191W | CV2III-350Y/72.5-10191W | CV2III-600Y/72.5-10191W ¦ CVIII-350Y/72.5-10191W ¦ SVIII-500Y/72.5-10191W | eligible |  | 133 | 72.5 | 1182 | 9 | Y | III
E-V260297-300 | CV |  |  |  | skip | no sold_type
E-CVT260001 | CVT | CVTIII-160D/12-0909 | CVTIII-160D/12-10091W | CVTIII-200D/12-10091W ¦ CZIII-500D/40.5-9 ¦ CZIII-600D/40.5-9 | family-i-um |  | 92.59 | 12 | 250 | 4 | D | III
E-CVT260002-005 | CVT |  |  |  | skip | no sold_type | 119.9 |  | 275
E-CVT260006 | CVT | CVTIII-200D/12-0909 |  |  | miss | Parameters out of catalogue range (current, Um, step voltage, or positions). | 88.88 | 12 | 500 |  | D | III | tap 0909 not a catalogue code; CVT envelope reject
E-CVT260007 | CVT |  |  |  | skip | no sold_type
E-CZ260001 | CZ | 3xCZI-500/40.5-7 | CZI-500/40.5-7 | CZI-600/40.5-7 | family-i-um |  | 197 | 40.5 | 700 |  | Y | I
E-CZ260002-003 | CZ | 3xCZI-500/40.5-9 | CZI-500/40.5-9 | CZI-600/40.5-9 | family-i-um |  | 56.1 | 40.5 | 825 |  | Y | I
E-CZ260004 | CZ | 3xCZI-500/40.5-17 |  |  | skip | no transformer I |  | 40.5 |  |  |  | I
E-CZ260005-006 | CZ | 3xCZI-500/40.5-5 | CZI-500/40.5-5 | CZI-600/40.5-5 | family-i-um |  | 173.6 | 40.5 | 530 |  | Y | I
E-CZ260007 | CZ | 3xCZI-500/40.5-9 | CZI-500/40.5-9 | CZI-600/40.5-9 | family-i-um |  | 17.5 | 40.5 | 893 |  | Y | I
E-CZ260008-009 | CZ | 3xCZI-500/40.5-17 | CZI-500/40.5-17 | CZI-600/40.5-17 | family-i-um |  | 25.3 | 40.5 | 375 |  | Y | I
E-CZ260010-011 | CZ |  |  |  | skip | no sold_type
E-CZ260012 | CZ | 3xCZI-500/40.5-17 |  |  | skip | no transformer I |  | 40.5 |  | 17 |  | I
E-CZ260013-014 | CZ |  |  |  | skip | no sold_type | 115.47 |  | 505 | 4
E-CZ260015 | CZ |  |  |  | skip | no sold_type
E-CZ260016 | CZ | 3xCZI-500/40.5-9 | CZI-500/40.5-9 | CZI-600/40.5-9 | family-i-um |  | 183 | 40.5 | 500 |  | Y | I
E-CZ260017-018 | CZ |  |  |  | skip | no sold_type | 111.89 |  | 359.69 | 4
E-HWV260001 | HWV | HWVIII-400Y/17.5-18353W | HWVIII-400Y/17.5-18353W | HWVIII-800Y/17.5-18353W ¦ 3xHWVI-400/17.5-18353W ¦ 3xHWVI-800/17.5-18353W | exact |  | 117.14 | 17.5 | 431.25 | 16 | Y | III
E-HWV260002 | HWV | HWVI-800Y/40.5-10193W | HWVI-800/40.5-10193W | HWVI-1000/40.5-10193W | exact |  | 460 | 40.5 | 0 | 8 | Y | I
E-HWV260003 | HWV | HWVIII-400D/72.5-18170 | HWVIII-400D/72.5-18170 | HWVIII-800D/72.5-18170 ¦ 3xHWVI-400/72.5-18170 ¦ 3xHWVI-800/72.5-18170 | exact |  | 102.9 | 72.5 | 825 |  | D | III
E-HWV260004 | HWV | HWVIII-800D/40.5-10193W |  |  | skip | no transformer I |  | 40.5 |  |  | D | III
E-HWV260005 | HWV |  |  |  | skip | no sold_type | 149.4 |  | 1182 | 9
E-HWV260006 | HWV | HWVIII-400Y/17.5-18353W | HWVIII-400Y/17.5-18353W | HWVIII-800Y/17.5-18353W ¦ 3xHWVI-400/17.5-18353W ¦ 3xHWVI-800/17.5-18353W | exact |  | 117.14 | 17.5 | 431.25 | 16 | Y | III
E-HWV260007-008 | HWV | HWVIII-1000D/40.5-1 | HWVIII-1000D/40.5-10010 | 3xHWVI-1000/40.5-10010 | family-i-um |  | 821.61 | 40.5 | 0 |  | D | III
E-SHZV260001 | SHZV | SHZVIII-1000Y/126D-10193W |  |  | skip | no transformer I |  | 126 |  |  | Y | III
E-SHZV260002 | SHZV | SHZVIII-600Y/170D-14273G | CM2III-500Y/170D-14273G | CM2III-600Y/170D-14273G ¦ SHZVIII-400Y/170D-14273G ¦ SHZVIII-600Y/170D-14273G | eligible |  | 384.1 | 170 | 2857.9 | 12 | Y | III
E-SHZV260003-009 | SHZV | SHZVIII-1000Y/126D-10183W |  |  | skip | no transformer I |  | 126 | 2500 |  | Y | III
E-SHZV260010-013 | SHZV | SHZVIII-1000Y/126D-10183W |  |  | skip | no transformer I |  | 126 | 2500 |  | Y | III
E-SHZV260014 | SHZV |  |  |  | skip | no sold_type
E-SHZV260015-019 | SHZV | SHZVIII-1000Y/72.5C-10193G | SHZVIII-1000Y/72.5B-10193G | SHZVGIII-1300Y/72.5B-10193G ¦ SHZVGIII-1500Y/72.5B-10193G ¦ 3xCM2I-1200/72.5B-10193G | family-i-um |  | 787.3 | 72.5 | 238.2 | 8 | Y | III
E-SHZV260020 | SHZV |  |  |  | skip | no sold_type | 615.84 |  | 187.5
E-SHZV260021-022 | SHZV | SHZVIII-600Y/126D-14273G | CM2III-500Y/126C-14273G | CM2III-600Y/126C-14273G ¦ SHZVIII-400Y/126C-14273G ¦ SHZVIII-600Y/126C-14273G | eligible |  | 180.4 | 126 | 2886.8 | 12 | Y | III
E-SHZV260023 | SHZV |  |  |  | skip | no sold_type
E-SHZV260024-043 | SHZV | SHZVIII-1000Y/72.5B-10191W |  |  | skip | no transformer I |  | 72.5 |  |  | Y | III
E-SHZV260044-045 | SHZV | SHZVIII-600Y/126D-14273G | CM2III-500Y/126C-14273G | CM2III-600Y/126C-14273G ¦ SHZVIII-400Y/126C-14273G ¦ SHZVIII-600Y/126C-14273G | eligible |  | 180.4 | 126 | 2886.8 | 12 | Y | III
E-SHZV260046 | SHZV |  |  |  | skip | no sold_type
E-SHZV260047-48 | SHZV | SHZVIII-1000Y/72.5B-10193G |  |  | skip | no transformer I |  | 72.5 |  |  | Y | III
E-SHZV260049 | SHZV | SHZVIII-1300Y/72.5D-12233G | SHZVGIII-1300Y/72.5B-12233G | SHZVGIII-1500Y/72.5B-12233G ¦ 3xCM2I-1200/72.5B-12233G ¦ 3xCM2I-1500/72.5B-12233G | miss |  | 1033.3 | 72.5 | 1039.2 | 10 | Y | III | sold SHZV-1300; catalogue III 1300 is SHZVG. Engine naming is right
E-SHZV260050-051 | SHZV | SHZVIII-400Y/72.5C-1223 | CM2III-500Y/72.5B-10193W | CM2III-600Y/72.5B-10193W ¦ SHZVIII-400Y/72.5B-10193W ¦ SHZVIII-600Y/72.5B-10193W | eligible |  | 196.8 | 72.5 | 2540.3 |  | Y | III
E-SHZV260052-073 | SHZV | SHZVIII-1000Y/126D-10183W |  |  | skip | no transformer I |  | 126 | 2500 |  | Y | III
E-SHZV260074-075 | SHZV |  |  |  | skip | no sold_type | 1321 |  | 2584 | 6
E-SHZV260076-077 | SHZV | SHZVIII-600Y/72.5-18353W | CM2III-500Y/72.5B-18353W | CM2III-600Y/72.5B-18353W ¦ SHZVIII-400Y/72.5B-18353W ¦ SHZVIII-600Y/72.5B-18353W | eligible |  | 346.4 | 72.5 | 1991.9 | 16 | Y | III
E-SHZV260079 | SHZV | SHZVIII-1000Y/72.5B-12233W |  |  | skip | no transformer I |  | 72.5 |  |  | Y | III
E-SHZV260080 | SHZV | SHZVIII-1000Y/126C-14273G | SHZVIII-1000Y/126C-14273G | SHZVGIII-1300Y/126C-14273G ¦ SHZVGIII-1500Y/126C-14273G ¦ 3xCM2I-800/126C-14273G | exact |  | 754 | 126 | 952 | 12 | Y | III
E-SHZV260081 | SHZV | SHZVIII-1000Y/72.5C-12111W |  |  | skip | no transformer I |  | 72.5 |  |  | Y | III
E-SHZV260082 | SHZV |  |  |  | skip | no sold_type | 1321 |  | 2584 | 6
E-SHZV260083-088 | SHZV | 3xSHZVI-2400Y/72.5D-10193 |  |  | skip | no transformer I |  | 72.5 |  |  | Y | I
E-SHZV260089-090 | SHZV | SHZVIII-1000Y/72.5B-18170 | SHZVIII-1000Y/72.5B-18170 | SHZVGIII-1300Y/72.5B-18170 ¦ SHZVGIII-1500Y/72.5B-18170 ¦ 3xCM2I-800/72.5B-18170 | exact |  | 721.7 | 72.5 | 1157.7 |  | Y | III
E-SHZV260091-092 | SHZV |  |  |  | skip | no sold_type | 747.16 |  | 1299.04
E-SHZV260093-094 | SHZV | SHZVIII-1000Y/72.5C-12111W | SHZVIII-1000Y/72.5B-12111W | SHZVGIII-1300Y/72.5B-12111W ¦ SHZVGIII-1500Y/72.5B-12111W ¦ 3xCM2I-800/72.5B-12111W | family-i-um |  | 673.8 | 72.5 | 1969 | 5 | Y | III
E-SHZV260095-098 | SHZV | SHZVIII-1000Y/72.5C-10193W | CM2III-600Y/72.5B-10193W | SHZVIII-600Y/72.5B-10193W ¦ SHZVIII-1000Y/72.5B-10193W ¦ SHZVGIII-1300Y/72.5B-10193W | eligible |  | 571 | 72.5 | 1624 | 8 | Y | III
E-SHZV260099-100 | SHZV | SHZVIII-400Y/252D-14273W | CM2III-500Y/252D-14273W | CM2III-600Y/252D-14273W ¦ SHZVIII-400Y/252D-14273W ¦ SHZVIII-600Y/252D-14273W | eligible |  | 194.5 | 252 | 1588 | 12 | Y | III
E-SHZV260101 | SHZV | SHZVIII-1000Y/72.5C-12111W | SHZVIII-1000Y/72.5B-12111W | SHZVGIII-1300Y/72.5B-12111W ¦ SHZVGIII-1500Y/72.5B-12111W ¦ 3xCM2I-1200/72.5B-12111W | family-i-um |  | 827.1 | 72.5 | 2511 | 5 | Y | III
E-SHZV260102 | SHZV | 3xSHZVI-1200/300D-12111W | SHZVI-1200/300DE-12111W | SHZVI-1500/300DE-12111W ¦ SHZVGI-1300/300DE-12111W ¦ SHZVGI-3000/300DE-12111W | family-i-um |  | 996.1 | 300 | 1860 | 5 | Y | I
E-SHZV260103 | SHZV | SHZVIII-600Y/170D-12233G |  |  | skip | no transformer I |  | 170 | 2878 | 10 | Y | III
E-SHZV260104 | SHZV | SHZVIII-1000Y/72.5B-14273W | SHZVIII-1000Y/72.5B-14273W | SHZVGIII-1300Y/72.5B-14273W ¦ SHZVGIII-1500Y/72.5B-14273W ¦ 3xCM2I-800/72.5B-14273W | exact |  | 654.3 | 72.5 | 866.03 | 12 | Y | III
E-SHZV260105 | SHZV | SHZVIII-1000Y/72.5C-14271W | CM2III-500Y/72.5B-14271W | CM2III-600Y/72.5B-14271W ¦ SHZVIII-600Y/72.5B-14271W ¦ SHZVIII-1000Y/72.5B-14271W | eligible |  | 446.1 | 72.5 | 1270 | 13 | Y | III
E-SHZV260106 | SHZV | SHZVI-1000/126D-10191W |  |  | skip | no transformer I |  | 126 |  |  |  | I
E-SHZV260107-108 | SHZV | SHZVIII-600Y/126D-14273G | CM2III-500Y/126C-14273G | CM2III-600Y/126C-14273G ¦ SHZVIII-400Y/126C-14273G ¦ SHZVIII-600Y/126C-14273G | eligible |  | 180.4 | 126 | 2886.8 | 12 | Y | III
E-SHZV260109-113 | SHZV | SHZVIII-600Y/126D-14273G | CM2III-500Y/126C-14273G | CM2III-600Y/126C-14273G ¦ SHZVIII-400Y/126C-14273G ¦ SHZVIII-600Y/126C-14273G | eligible |  | 180.4 | 126 | 2886.8 | 12 | Y | III
E-SHZV260114 | SHZV |  |  |  | skip | no sold_type | 546.7 |  | 1524.2
E-SHZV260116 | SHZV | SHZVIII-600Y/126D-14273G | CM2III-500Y/126C-14273G | CM2III-600Y/126C-14273G ¦ SHZVIII-400Y/126C-14273G ¦ SHZVIII-600Y/126C-14273G | eligible |  | 180.4 | 126 | 2886.8 | 12 | Y | III
E-SHZV260117-119 | SHZV | SHZVIII-1000Y/72.5B-10191W |  |  | skip | no transformer I |  | 72.5 |  |  | Y | III
E-SHZV260120-125 | SHZV | SHZVIII-600Y/126D-14273G | CM2III-500Y/126C-14273G | CM2III-600Y/126C-14273G ¦ SHZVIII-400Y/126C-14273G ¦ SHZVIII-600Y/126C-14273G | eligible |  | 180.4 | 126 | 2886.8 | 12 | Y | III
E-SHZV260129-130 | SHZV | SHZVIII-1000Y/72.5B-12111W | SHZVIII-1000Y/72.5B-12111W | SHZVGIII-1300Y/72.5B-12111W ¦ SHZVGIII-1500Y/72.5B-12111W ¦ 3xCM2I-800/72.5B-12111W | exact |  | 631.8 | 72.5 | 1905 | 5 | Y | III
E-SHZV260131 | SHZV | SHZVIII-1000Y/72.5B-18353W | SHZVIII-1000Y/72.5B-18353W | SHZVGIII-1300Y/72.5B-18353W ¦ SHZVGIII-1500Y/72.5B-18353W ¦ 3xCM2I-800/72.5B-18353W | exact |  | 734.47 | 72.5 | 49.796 | 16 | Y | III
E-SHZV260132 | SHZV | SHZVIII-1000Y/170D-12233W | SHZVIII-1000Y/170D-12233W | SHZVGIII-1300Y/170D-12233W ¦ SHZVGIII-1500Y/170D-12233W ¦ 3xCM2I-800/170D-12233W | exact |  | 720 | 170 | 1588 | 10 | Y | III
E-SHZV260133 | SHZV |  |  |  | skip | no sold_type
E-S260001-002 | SY | SYXZZ-40.5-200-9 |  |  | skip | unparsed sold_type |  | 40.5
E-S260003-008 | SY | SYXZZ-40.5-200-9 |  |  | skip | unparsed sold_type |  | 40.5
E-S260009-018 | SY | SYXZZ-40.5-200-9 |  |  | skip | unparsed sold_type |  | 40.5
E-S260019-028 | SY | SYXZZ-40.5-200-9 |  |  | skip | unparsed sold_type |  | 40.5
E-S260029 | SY | SYXZZ-40.5-20-0 |  |  | skip | unparsed sold_type | 109.5 | 40.5 | 505 | 4
E-S260029 | SY | SYXZZ-40.5-20-0 |  |  | skip | unparsed sold_type | 109.5 | 40.5 | 505 | 4
E-S260030-031 | SY | SYXZZ-40.5-20-0 |  |  | skip | unparsed sold_type | 109 | 40.5 | 505 | 4
E-S260032-033 | SY | WDGV-800/40.5-6x5 |  |  | skip | unparsed sold_type |  | 40.5 |  |  |  | V
E-S260034 | SY |  |  |  | skip | no sold_type
E-S260035-036 | SY | SYXZZ-40.5-20-0 |  |  | skip | unparsed sold_type | 45.8 | 40.5 | 510 | 4
E-S260037-038 | SY | SYXZZ-40.5-20-0 |  |  | skip | unparsed sold_type | 73.3 | 40.5 | 510 | 4
E-S260039-040 | SY | SYXZZ-40.5-20-0 |  |  | skip | unparsed sold_type | 115.5 | 40.5 | 510 | 4
E-S260041-050 | SY |  |  |  | skip | no sold_type
E-S260051-053 | SY | CVIII-350Y/40.5-10193W |  |  | skip | no transformer I |  | 40.5 |  |  | Y | III
E-S260054-063 | SY |  |  |  | skip | no sold_type
E-S260064-065 | SY |  |  |  | skip | no sold_type
E-S260066 | SY | CVIII-350Y/72.5-10191W |  |  | skip | no transformer I |  | 72.5 |  |  | Y | III
E-S260067-074 | SY |  |  |  | skip | no sold_type
E-CM2260001-002 | VCM | CM2III-500Y/72.5C-12233G |  |  | skip | no transformer I |  | 72.5 |  |  | Y | III
E-CM2260003-004 | VCM | CM2III-500Y/170B-14273G |  |  | skip | no transformer I |  | 170 |  |  | Y | III
E-CM2260005-008 | VCM | CM2III-500Y/170B-14273G |  |  | skip | no transformer I |  | 170 |  |  | Y | III
E-CM2260009 | VCM | CM2III-500Y/170B-18171W |  |  | skip | no transformer I |  | 170 |  |  | Y | III
E-CM2260010 | VCM | CM2III-500Y/72.5B-10193W | CV2III-350Y/72.5-10193W | CV2III-600Y/72.5-10193W ¦ CM2III-500Y/72.5B-10193W ¦ CM2III-600Y/72.5B-10193W | eligible |  | 179.62 | 72.5 | 1624 | 8 | Y | III
E-CM2260011-012 | VCM | CM2I-500/252D-18353W | CM2I-500/252D-18353W | CM2I-600/252D-18353W ¦ SHZVI-400/252D-18353W ¦ SHZVI-600/252D-18353W | exact |  | 65 | 252 | 1471 | 16 | Y | I
E-CM2260013-032 | VCM | CM2III-600Y/72.5C-14273G | CM2III-500Y/72.5B-14273G | CM2III-600Y/72.5B-14273G ¦ SHZVIII-400Y/72.5B-14273G ¦ SHZVIII-600Y/72.5B-14273G | family |  | 234.3 | 72.5 | 1111.4 | 12 | Y | III
E-CM2260033-067 | VCM | CM2III-600Y/72.5C-14273G | CM2III-500Y/72.5B-14273G | CM2III-600Y/72.5B-14273G ¦ SHZVIII-400Y/72.5B-14273G ¦ SHZVIII-600Y/72.5B-14273G | family |  | 234.3 | 72.5 | 1111.4 | 12 | Y | III
E-CM2260068-112 | VCM | CM2III-600Y/72.5C-14273G | CM2III-500Y/72.5B-14273G | CM2III-600Y/72.5B-14273G ¦ SHZVIII-400Y/72.5B-14273G ¦ SHZVIII-600Y/72.5B-14273G | family |  | 374.9 | 72.5 | 1111.4 | 12 | Y | III
E-CM2260113 | VCM | CM2III-500Y/72.5B-14271W | CM2III-500Y/72.5B-14271W | CM2III-600Y/72.5B-14271W ¦ SHZVIII-400Y/72.5B-14271W ¦ SHZVIII-600Y/72.5B-14271W | exact |  | 248.86 | 72.5 | 565 | 13 | Y | III
E-CM2260115-116 | VCM |  |  |  | skip | no sold_type | 294.34 |  | 1299.04
E-CM2260117 | VCM | CM2III-500Y/72.5B-14271W | CM2III-500Y/72.5B-14271W | CM2III-600Y/72.5B-14271W ¦ SHZVIII-400Y/72.5B-14271W ¦ SHZVIII-600Y/72.5B-14271W | exact |  | 218.69 | 72.5 | 381.05 | 13 | Y | III
E-CM2260118 | VCM | CM2III-300Y/170B-12233W | CM2III-500Y/170D-12233W | CM2III-600Y/170D-12233W ¦ SHZVIII-400Y/170D-12233W ¦ SHZVIII-600Y/170D-12233W | family |  | 88 | 170 | 1082.5 | 10 | Y | III
E-CM2260119 | VCM |  |  |  | skip | no sold_type
E-CM2260120 | VCM | 3xCM2I-1500/72.5B-10193W |  |  | skip | no transformer I |  | 72.5 | 360 |  |  | I
E-CM2260121 | VCM | CM2III-500Y/72.5C-14273W | CM2III-500Y/72.5B-14273W | CM2III-600Y/72.5B-14273W ¦ SHZVIII-400Y/72.5B-14273W ¦ SHZVIII-600Y/72.5B-14273W | family-i-um |  | 264.2 | 72.5 | 1328 | 12 | Y | III
E-CM2260122 | VCM | CM2III-500Y/72.5C-14273W | CM2III-500Y/72.5B-14273W | CM2III-600Y/72.5B-14273W ¦ SHZVIII-400Y/72.5B-14273W ¦ SHZVIII-600Y/72.5B-14273W | family-i-um |  | 166.5 | 72.5 | 1328 | 12 | Y | III
E-CM2260123-124 | VCM |  |  |  | skip | no sold_type | 162.1 |  | 952.6
E-CM2260125-126 | VCM | CM2III-500Y/170B-14273G |  |  | skip | no transformer I |  | 170 |  |  | Y | III
E-CM2260127-136 | VCM | CM2III-600Y/72.5C-14273G | CM2III-500Y/72.5B-14273G | CM2III-600Y/72.5B-14273G ¦ SHZVIII-400Y/72.5B-14273G ¦ SHZVIII-600Y/72.5B-14273G | family |  | 374.9 | 72.5 | 1111.4 | 12 | Y | III
E-CM2260137-138 | VCM | CM2III-500Y/126B-14273G | CM2III-500Y/126C-14273G | CM2III-600Y/126C-14273G ¦ SHZVIII-400Y/126C-14273G ¦ SHZVIII-600Y/126C-14273G | family-i-um |  | 128.6 | 126 | 953 | 12 | Y | III
E-CM2260139 | VCM | CM2III-500Y/126B-12231W | CV2III-600Y/126-12231W | CM2III-500Y/126C-12231W ¦ CM2III-600Y/126C-12231W ¦ SHZVIII-400Y/126C-12231W | eligible |  | 355.4 | 126 | 664 | 11 | Y | III
E-CM2260140 | VCM | CM2III-500Y/72.5C-14273W | CM2III-500Y/72.5B-14273W | CM2III-600Y/72.5B-14273W ¦ SHZVIII-600Y/72.5B-14273W ¦ SHZVIII-1000Y/72.5B-14273W | family-i-um |  | 423 | 72.5 | 1328 | 12 | Y | III
E-CM2260141 | VCM | 3xCM2I-1500/170B-14131W | CM2I-1500/170D-14131W | SHZVI-1500/170D-14131W ¦ SHZVI-1600/170D-14131W ¦ SHZVGI-3000/170D-14131W | family-i-um |  | 1356 | 170 | 1346 | 6 | Y | I
E-CM2260142-143 | VCM | CM2I-600/72.5C-12233W | CV2I-350/72.5-12233W | CV2I-600/72.5-12233W ¦ CM2I-500/72.5B-12233W ¦ CM2I-600/72.5B-12233W | eligible |  | 290.9 | 72.5 | 800 | 10 | Y | I
E-CM2260144 | VCM | CM2III-500Y/72.5B-14271W | CM2III-500Y/72.5B-14271W | CM2III-600Y/72.5B-14271W ¦ SHZVIII-400Y/72.5B-14271W ¦ SHZVIII-600Y/72.5B-14271W | exact |  | 163.4 | 72.5 | 306 | 13 | Y | III
E-CM2260145 | VCM | CM2III-500Y/72.5B-14273G | CM2III-500Y/72.5B-14273G | CM2III-600Y/72.5B-14273G ¦ SHZVIII-600Y/72.5B-14273G ¦ SHZVIII-1000Y/72.5B-14273G | exact |  | 453 | 72.5 | 433 | 12 | Y | III
E-CM2260146-148 | VCM | CM2III-500Y/170B-14273G |  |  | skip | no transformer I |  | 170 |  |  | Y | III
E-CM2260149-150 | VCM | CM2III-500Y/170D-12233W |  |  | skip | no transformer I |  | 170 |  |  | Y | III
E-CM2260151 | VCM | 3xCM2I-1500/72.5C-16160 | CM2I-1500/72.5B-16160 | SHZVI-1500/72.5B-16160 ¦ SHZVI-1600/72.5B-16160 ¦ SHZVGI-3000/72.5B-16160 | family-i-um |  | 1429 | 72.5 | 1832 |  | Y | I
E-CM2260152 | VCM | CM2III-600Y/72.5B-10191W | CV2III-600Y/72.5-10191W | CM2III-600Y/72.5B-10191W ¦ SHZVIII-600Y/72.5B-10191W ¦ SHZVIII-1000Y/72.5B-10191W | eligible |  | 530 | 72.5 | 1181 | 9 | Y | III
E-CM2260153 | VCM |  |  |  | skip | no sold_type
E-CM2260154 | VCM | CM2III-500Y/126C-10193W |  |  | skip | no transformer I |  | 126 |  |  | Y | III
E-CM2260155-157 | VCM | CM2I-600Y/170C-12233W | CM2I-800/170D-12233W | CM2I-1200/170D-12233W ¦ SHZVI-1000/170D-12233W ¦ SHZVI-1200/170D-12233W | family |  | 591.4 | 170 | 1985 | 10 | Y | I
E-CM2260158 | VCM | CM2III-500Y/126C-10193W |  |  | skip | no transformer I |  | 126 |  |  | Y | III
E-CM2260159 | VCM | CM2III-500Y/170C-12233G | CM2III-500Y/170D-12233G | CM2III-600Y/170D-12233G ¦ SHZVIII-400Y/170D-12233G ¦ SHZVIII-600Y/170D-12233G | family-i-um |  | 271.7 | 170 | 1299 | 10 | Y | III
E-CM2260160-164 | VCM | CM2III-500Y/170C-14273W |  |  | skip | no transformer I |  | 170 |  |  | Y | III
E-CM2260165-167 | VCM | CM2III-500Y/170C-14273W |  |  | skip | no transformer I |  | 170 |  |  | Y | III
E-CM2260168 | VCM | CM2III-500Y/72.5C-18353W | CM2III-500Y/72.5B-18353W | CM2III-600Y/72.5B-18353W ¦ SHZVIII-400Y/72.5B-18353W ¦ SHZVIII-600Y/72.5B-18353W | family-i-um |  | 238.47 | 72.5 | 1437.5 | 16 | Y | III
E-CM2260169 | VCM |  |  |  | skip | no sold_type
E-CM2260170 | VCM | CM2III-500Y/72.5B-18353W |  |  | skip | no transformer I |  | 72.5 |  |  | Y | III
E-CM2260171-180 | VCM | CM2III-600Y/72.5C-14273G | CM2III-500Y/72.5B-14273G | CM2III-600Y/72.5B-14273G ¦ SHZVIII-400Y/72.5B-14273G ¦ SHZVIII-600Y/72.5B-14273G | family |  | 374.9 | 72.5 | 1111.4 | 12 | Y | III
E-CM2260181 | VCM | CM2III-300Y/170B-10191W | CM2III-500Y/170D-10191W | CM2III-600Y/170D-10191W ¦ SHZVIII-400Y/170D-10191W ¦ SHZVIII-600Y/170D-10191W | family |  | 109.3 | 170 | 1995 | 9 | Y | III
E-CM2260182 | VCM |  |  |  | skip | no sold_type
E-CM2260183 | VCM | CM2III-500Y/126D-14271G |  |  | skip | no transformer I |  | 126 |  |  | Y | III
E-CM2260184-203 | VCM | CM2III-600Y/72.5C-14273G | CM2III-500Y/72.5B-14273G | CM2III-600Y/72.5B-14273G ¦ SHZVIII-400Y/72.5B-14273G ¦ SHZVIII-600Y/72.5B-14273G | family |  | 374.9 | 72.5 | 1111.4 | 12 | Y | III
E-CM2260204 | VCM | CM2III-500Y/72.5B-10191W | CV2III-600Y/72.5-10191W | CM2III-500Y/72.5B-10191W ¦ CM2III-600Y/72.5B-10191W ¦ SHZVIII-600Y/72.5B-10191W | eligible |  | 424.2 | 72.5 | 1182 | 9 | Y | III
E-CM2260205 | VCM |  |  |  | skip | no sold_type
E-CM2260206 | VCM |  |  |  | skip | no sold_type | 257.3 |  | 476.3
E-CM2260207 | VCM | CM2III-600Y/170B-12233W | CM2III-600Y/170D-12233W | SHZVIII-600Y/170D-12233W ¦ SHZVIII-1000Y/170D-12233W ¦ SHZVGIII-1300Y/170D-12233W | family-i-um |  | 505.9 | 170 | 1082 | 10 | Y | III
E-CM2260208 | VCM |  |  |  | skip | no sold_type
E-CM2260209 | VCM |  |  |  | skip | no sold_type
E-CM2260210-213 | VCM | CM2I-1500/170D-22433W |  |  | miss | Parameters out of catalogue range (current, Um, step voltage, or positions). | 1030 | 170 | 0 | 20 | Y | I | tap 22433W pitch 22 does not exist
E-CM2260214-219 | VCM | CM2III-500Y/72.5B-10181W | CV2III-350Y/72.5-10191W | CV2III-600Y/72.5-10191W ¦ CM2III-500Y/72.5B-10191W ¦ CM2III-600Y/72.5B-10191W | eligible |  | 294.34 | 72.5 | 1299.04 | 9 | Y | III
E-CM2260220-222 | VCM | CM2III-500Y/72.5B-14273G |  |  | skip | no transformer I |  | 72.5 |  |  | Y | III
E-CM2260223 | VCM |  |  |  | skip | no sold_type | 131 |  | 915
E-CM2260224-225 | VCM | CM2III-600Y/72.5B-10193W |  |  | skip | no transformer I |  | 72.5 |  |  | Y | III
E-CM2260226-227 | VCM | 3xCM2I-1500/170B-14131W | CM2I-1500/170D-14131W | SHZVI-1500/170D-14131W ¦ SHZVI-1600/170D-14131W ¦ SHZVGI-3000/170D-14131W | family-i-um |  | 1356 | 170 | 1346 | 6 | Y | I
E-CM2260228 | VCM | CM2III-500Y/72.5B-14273G |  |  | skip | no transformer I |  | 72.5 |  |  | Y | III
E-CM2260229 | VCM | CM2III-600Y/72.5B-12231G | CV2III-350Y/72.5-12231G | CV2III-600Y/72.5-12231G ¦ CM2III-500Y/72.5B-12231G ¦ CM2III-600Y/72.5B-12231G | eligible |  | 349.91 | 72.5 | 571.58 | 11 | Y | III
E-CM2260230 | VCM | CM2III-500Y/170B-12233W | CM2III-500Y/170D-12233W | CM2III-600Y/170D-12233W ¦ SHZVIII-400Y/170D-12233W ¦ SHZVIII-600Y/170D-12233W | family-i-um |  | 181.1 | 170 | 1875 | 10 | Y | III
E-CM2260231-232 | VCM | CM2III-500Y/72.5B-14273W | CM2III-500Y/72.5B-14273W | CM2III-600Y/72.5B-14273W ¦ SHZVIII-400Y/72.5B-14273W ¦ SHZVIII-600Y/72.5B-14273W | exact |  | 104.59 | 72.5 | 1328 | 12 | Y | III
E-CM2260233-236 | VCM | CM2III-500Y/72.5B-10191W | CV2III-600Y/72.5-10191W | CM2III-500Y/72.5B-10191W ¦ CM2III-600Y/72.5B-10191W ¦ SHZVIII-600Y/72.5B-10191W | eligible |  | 424.2 | 72.5 | 0 | 9 | Y | III
E-CM2260237 | VCM | CM2III-500Y/170B-12233W | CM2III-500Y/170D-12233W | CM2III-600Y/170D-12233W ¦ SHZVIII-600Y/170D-12233W ¦ SHZVIII-1000Y/170D-12233W | family-i-um |  | 423.4 | 170 | 1082.5 | 10 | Y | III
E-CM2260238 | VCM | CM2III-300Y/170B-12233W | CM2III-500Y/170D-12233W | CM2III-600Y/170D-12233W ¦ SHZVIII-400Y/170D-12233W ¦ SHZVIII-600Y/170D-12233W | family |  | 144.3 | 170 | 952 | 10 | Y | III
E-CM2260239 | VCM |  |  |  | skip | no sold_type
E-CM2260240-249 | VCM | CM2III-600Y/72.5C-14273G | CM2III-500Y/72.5B-14273G | CM2III-600Y/72.5B-14273G ¦ SHZVIII-400Y/72.5B-14273G ¦ SHZVIII-600Y/72.5B-14273G | family |  | 234.3 | 72.5 | 1111.4 | 12 | Y | III
E-CM2260250-256 | VCM | CM2I-500D/72.5B-14273W | CM2I-500/72.5B-14273W | CM2I-600/72.5B-14273W ¦ SHZVI-400/72.5B-14273W ¦ SHZVI-600/72.5B-14273W | exact |  | 176 | 72.5 | 929.6 | 12 | D | I
E-CM2260257 | VCM | CM2III-600Y/72.5B-10193W | CV2III-600Y/72.5-10193W | CM2III-600Y/72.5B-10193W ¦ SHZVIII-600Y/72.5B-10193W ¦ SHZVIII-1000Y/72.5B-10193W | eligible |  | 520.6 | 72.5 | 249 | 8 | Y | III
E-CM2260258 | VCM |  |  |  | skip | no sold_type | 227.5 |  | 1875
E-CM2260259 | VCM | CM2III-500Y/72.5C-10191G | CV2III-600Y/72.5-10191G | CM2III-500Y/72.5B-10191G ¦ CM2III-600Y/72.5B-10191G ¦ SHZVIII-600Y/72.5B-10191G | eligible |  | 418.38 | 72.5 | 1180.5 | 9 | Y | III
E-CM2260260-261 | VCM | CM2III-500Y/170C-10193W | CM2III-500Y/170D-10193W | CM2III-600Y/170D-10193W ¦ SHZVIII-400Y/170D-10193W ¦ SHZVIII-600Y/170D-10193W | family-i-um |  | 233.3 | 170 | 1587.7 | 8 | Y | III
E-CM2260262 | VCM | CM2III-500Y/126B-10191W | CV2III-350Y/126-10191W | CV2III-600Y/126-10191W ¦ CM2III-500Y/126C-10191W ¦ CM2III-600Y/126C-10191W | eligible |  | 316.29 | 126 | 1183 | 9 | Y | III
E-CM2260263 | VCM |  |  |  | skip | no sold_type | 156.19 |  | 414.97 | 16
E-CM2260263 | VCM |  |  |  | skip | no sold_type | 156.19 |  | 414.97 | 16
E-CM2260264-265 | VCM | CM2III-500Y/170B-12233W | CM2III-500Y/170D-12233W | CM2III-600Y/170D-12233W ¦ SHZVIII-600Y/170D-12233W ¦ SHZVIII-1000Y/170D-12233W | family-i-um |  | 483.9 | 170 | 1082.5 | 10 | Y | III
E-CM2260266 | VCM |  |  |  | skip | no sold_type
E-CM2260267 | VCM | 3xCM2I-1500/72.5B-18180 |  |  | skip | no transformer I |  | 72.5 | 798 |  |  | I
E-CM2260268-270 | VCM | CM2III-600Y/72.5B-12233W | CV2III-600Y/72.5-12233W | CM2III-500Y/72.5B-12233W ¦ CM2III-600Y/72.5B-12233W ¦ SHZVIII-400Y/72.5B-12233W | eligible |  | 376.5 | 72.5 | 1328 | 10 | Y | III
E-CM2260271-272 | VCM | CM2III-500Y/252D-16313G | CM2III-500Y/252D-16313G | CM2III-600Y/252D-16313G ¦ SHZVIII-600Y/252D-16313G ¦ SHZVIII-1000Y/252D-16313G | exact |  | 403.5 | 252 | 917.9 | 14 | Y | III
E-CM2260273 | VCM | 3xCM2I-1200/170C-14131W | CM2I-1200/170D-14131W | CM2I-1500/170D-14131W ¦ SHZVI-1200/170D-14131W ¦ SHZVI-1500/170D-14131W | family-i-um |  | 1063 | 170 | 1328 | 6 | Y | I
E-CM2260274-277 | VCM | 3xCM2I-1200/170C-14130 |  |  | skip | no transformer I |  | 170 |  |  |  | I
E-CM2260278 | VCM | 3xCM2I-1200/170C-14130 |  |  | skip | no transformer I |  | 170 |  |  |  | I
E-CM2260279 | VCM | CM2III-500Y/72.5B-14271W | CM2III-500Y/72.5B-14271W | CM2III-600Y/72.5B-14271W ¦ SHZVIII-400Y/72.5B-14271W ¦ SHZVIII-600Y/72.5B-14271W | exact |  | 65.61 | 72.5 | 381.05 | 13 | Y | III
E-CM2260280-281 | VCM | CM2III-500Y/72.5C-14273W | CM2III-500Y/72.5B-14273W | CM2III-600Y/72.5B-14273W ¦ SHZVIII-400Y/72.5B-14273W ¦ SHZVIII-600Y/72.5B-14273W | family-i-um |  | 167 | 72.5 | 1328 | 12 | Y | III
E-CM2260282-283 | VCM | CM2III-500Y/72.5B-14273W | CM2III-500Y/72.5B-14273W | CM2III-600Y/72.5B-14273W ¦ SHZVIII-400Y/72.5B-14273W ¦ SHZVIII-600Y/72.5B-14273W | exact |  | 167 | 72.5 | 1328 | 12 | Y | III
E-CM2260284 | VCM | CM2III-500Y/170D-14273G | CM2III-500Y/170D-14273G | CM2III-600Y/170D-14273G ¦ SHZVIII-400Y/170D-14273G ¦ SHZVIII-600Y/170D-14273G | exact |  | 313.78 | 170 | 1660 | 12 | Y | III
E-CM2260285 | VCM |  |  |  | skip | no sold_type
E-CV2260001-004 | VCV | CV2III-350D/145-10193W | CV2III-350D/145-10193W | CV2III-600D/145-10193W ¦ CM2III-500D/170D-10193W ¦ CM2III-600D/170D-10193W | exact |  | 64.26 | 145 | 1725 | 8 | D | III
E-CV2260005-006 | VCV | CV2III-350D/145-10193W | CV2III-350D/145-10193W | CV2III-600D/145-10193W ¦ CM2III-500D/170D-10193W ¦ CM2III-600D/170D-10193W | exact |  | 64.25 | 145 | 1725 | 8 | D | III
E-CV2260007 | VCV | CV2III-350D/72.5-10193W | CV2III-350D/72.5-10193W | CV2III-600D/72.5-10193W ¦ CM2III-500D/72.5B-10193W ¦ CM2III-600D/72.5B-10193W | exact |  | 128.5 | 72.5 | 862.5 | 8 | D | III
E-CV2260008-009 | VCV | CV2III-350Y/72.5-10193W | CV2III-350Y/72.5-10193W | CV2III-600Y/72.5-10193W ¦ CM2III-500Y/72.5B-10193W ¦ CM2III-600Y/72.5B-10193W | exact |  | 167.3 | 72.5 | 747 | 8 | Y | III
E-CV2260010-014 | VCV | CV2III-350D/72.5-10193W | CV2III-350D/72.5-10193W | CV2III-600D/72.5-10193W ¦ CM2III-500D/72.5B-10193W ¦ CM2III-600D/72.5B-10193W | exact |  | 96.6 | 72.5 | 862.5 | 8 | D | III
E-CV2260015 | VCV | CV2III-350Y/72.5-10193W | CV2III-350Y/72.5-10193W | CV2III-600Y/72.5-10193W ¦ CM2III-500Y/72.5B-10193W ¦ CM2III-600Y/72.5B-10193W | exact |  | 111.3 | 72.5 | 995.9 | 8 | Y | III
E-CV2260016 | VCV | CV2III-350D/40.5-10193W | CV2III-350D/40.5-10193W | CV2III-600D/40.5-10193W ¦ CM2III-500D/72.5B-10193W ¦ CM2III-600D/72.5B-10193W | exact |  | 120.8 | 40.5 | 431.25 | 8 | D | III
E-CV2260017 | VCV | CV2III-600Y/40.5-10193W | CV2III-350Y/40.5-10193W | CV2III-600Y/40.5-10193W ¦ CM2III-500Y/72.5B-10193W ¦ CM2III-600Y/72.5B-10193W | family |  | 334.7 | 40.5 | 862.5 | 8 | Y | III
E-CV2260018 | VCV | CV2III-350D/145-10193W | CV2III-350D/145-10193W | CV2III-600D/145-10193W ¦ CM2III-500D/170D-10193W ¦ CM2III-600D/170D-10193W | exact |  | 30.2 | 145 | 1725 | 8 | D | III
E-CV2260019 | VCV | CV2III-350Y/72.5-10193W | CV2III-350Y/72.5-10193W | CV2III-600Y/72.5-10193W ¦ CM2III-500Y/72.5B-10193W ¦ CM2III-600Y/72.5B-10193W | exact |  | 222.6 | 72.5 | 497.68 | 8 | Y | III
E-CV2260020 | VCV | CV2III-350D/72.5-10193W | CV2III-350D/72.5-10193W | CV2III-600D/72.5-10193W ¦ CM2III-500D/72.5B-10193W ¦ CM2III-600D/72.5B-10193W | exact |  | 181.5 | 72.5 | 1089 | 8 | D | III
E-CV2260021 | VCV | CV2III-350Y/72.5-10193W |  |  | skip | no transformer I |  | 72.5 |  |  | Y | III
E-CV2260022-023 | VCV | CV2III-350D/40.5-12231W | CV2III-350D/40.5-12231W | CV2III-600D/40.5-12231W ¦ CM2III-500D/72.5B-12231W ¦ CM2III-600D/72.5B-12231W | exact |  | 122 | 40.5 | 450 | 11 | D | III
E-CV2260024 | VCV | CV2III-600D/145-10193W | CV2III-600D/145-10193W | CM2III-500D/170D-10193W ¦ CM2III-600D/170D-10193W ¦ SHZVIII-400D/170D-10193W | exact |  | 342 | 145 | 1048 | 8 | D | III
E-CV2260025-029 | VCV | CV2III-600Y/72.5-10191W |  |  | skip | no transformer I |  | 72.5 |  |  | Y | III
E-CV2260030 | VCV | CV2III-350Y/72.5-12233W | CV2III-350Y/72.5-12233W | CV2III-600Y/72.5-12233W ¦ CM2III-500Y/72.5B-12233W ¦ CM2III-600Y/72.5B-12233W | exact |  | 104.6 | 72.5 | 797 | 10 | Y | III
E-CV2260031-037 | VCV | CV2III-350D/145-10193W |  |  | skip | no transformer I |  | 145 |  |  | D | III
E-CV2260038-039 | VCV | CV2III-350D/72.5-10193W |  |  | skip | no transformer I |  | 72.5 |  |  | D | III
E-CV2260040 | VCV | CV2III-350Y/72.5-12231W |  |  | skip | no transformer I |  | 72.5 |  |  | Y | III
E-CV2260041-043 | VCV | CV2III-350D/72.5-10193W |  |  | skip | no transformer I |  | 72.5 |  |  | D | III
E-CV2260044-045 | VCV | CV2III-350D/145-10193W |  |  | skip | no transformer I |  | 145 |  |  | D | III
E-CV2260046 | VCV | CV2III-350D/145-10193W |  |  | skip | no transformer I |  | 145 |  |  | D | III
E-CV2260047 | VCV | CV2III-350Y/72.5-10193G | CV2III-350Y/72.5-10193G | CV2III-600Y/72.5-10193G ¦ CM2III-500Y/72.5B-10193G ¦ CM2III-600Y/72.5B-10193G | exact |  | 256.6 | 72.5 | 0 | 8 | Y | III
E-CV2260048-049 | VCV | CV2III-350Y/72.5-10193W | CV2III-350Y/72.5-10193W | CV2III-600Y/72.5-10193W ¦ CM2III-500Y/72.5B-10193W ¦ CM2III-600Y/72.5B-10193W | exact |  | 222.57 | 72.5 | 498 | 8 | Y | III
E-CV2260050 | VCV | CV2III-350Y/72.5-10193G | CV2III-350Y/72.5-10193G | CV2III-600Y/72.5-10193G ¦ CM2III-500Y/72.5B-10193G ¦ CM2III-600Y/72.5B-10193G | exact |  | 128.3 | 72.5 | 0 | 8 | Y | III
E-CV2260051-052 | VCV | CV2III-350Y/72.5-10193W |  |  | skip | no transformer I |  | 72.5 |  |  | Y | III
E-CV2260053-054 | VCV | CV2III-350Y/72.5-10191W | CV2III-350Y/72.5-10191W | CV2III-600Y/72.5-10191W ¦ CM2III-500Y/72.5B-10191W ¦ CM2III-600Y/72.5B-10191W | exact |  | 212.1 | 72.5 | 1182 | 9 | Y | III
E-CV2260055-056 | VCV | CV2III-600Y/72.5-10191W |  |  | skip | no transformer I |  | 72.5 |  |  | Y | III
E-CV2260057 | VCV | CV2III-600Y/72.5-1 |  |  | skip | no transformer I |  | 72.5 |  |  | Y | III
E-CV2260058 | VCV | CV2III-350Y/72.5-12233W | CV2III-350Y/72.5-12233W | CV2III-600Y/72.5-12233W ¦ CM2III-500Y/72.5B-12233W ¦ CM2III-600Y/72.5B-12233W | exact |  | 138 | 72.5 | 363.7 | 10 | Y | III
E-CV2260059-060 | VCV | CV2III-600D/40.5-10193G | CV2III-600D/40.5-10193G | CM2III-500D/72.5B-10193G ¦ CM2III-600D/72.5B-10193G ¦ SHZVIII-600D/72.5B-10193G | exact |  | 415.3 | 40.5 | 412.5 | 8 | D | III
E-CV2260061 | VCV | CV2III-350Y/72.5-10191W |  |  | skip | no transformer I |  | 72.5 |  |  | Y | III
E-CV2260062-064 | VCV | CV2III-350Y/126-10193W |  |  | skip | no transformer I |  | 126 |  |  | Y | III
E-CV2260065-066 | VCV | CV2III-350D/145-10193W | CV2III-350D/145-10193W | CV2III-600D/145-10193W ¦ CM2III-500D/170D-10193W ¦ CM2III-600D/170D-10193W | exact |  | 30.2 | 145 | 1725 | 8 | D | III
E-CV2260067 | VCV | CV2III-350Y/72.5-10193W | CV2III-350Y/72.5-10193W | CV2III-600Y/72.5-10193W ¦ CM2III-500Y/72.5B-10193W ¦ CM2III-600Y/72.5B-10193W | exact |  | 209.18 | 72.5 | 996 | 8 | Y | III
E-CV2260068-069 | VCV | CV2III-350D/145-10193W | CV2III-350D/145-10193W | CV2III-600D/145-10193W ¦ CM2III-500D/170D-10193W ¦ CM2III-600D/170D-10193W | exact |  | 96.6 | 145 | 1725 | 8 | D | III
E-CV2260070-071 | VCV |  |  |  | skip | no sold_type
E-CV2260072 | VCV | CV2III-600D/40.5-10193W | CV2III-600D/40.5-10193W | CM2III-600D/72.5B-10193W ¦ SHZVIII-600D/72.5B-10193W ¦ SHZVIII-1000D/72.5B-10193W | exact |  | 563 | 40.5 | 236.3 | 8 | D | III
E-CV2260073 | VCV | CV2III-350D/145-10193W | CV2III-350D/145-10193W | CV2III-600D/145-10193W ¦ CM2III-500D/170D-10193W ¦ CM2III-600D/170D-10193W | exact |  | 48.3 | 145 | 1725 | 8 | D | III
E-CV2260074 | VCV | CV2III-350D/72.5-10193W | CV2III-350D/72.5-10193W | CV2III-600D/72.5-10193W ¦ CM2III-500D/72.5B-10193W ¦ CM2III-600D/72.5B-10193W | exact |  | 60.37 | 72.5 | 862.5 | 8 | D | III
E-CV2260075-076 | VCV | CV2III-350D/72.5-10193W | CV2III-350D/72.5-10193W | CV2III-600D/72.5-10193W ¦ CM2III-500D/72.5B-10193W ¦ CM2III-600D/72.5B-10193W | exact |  | 60.37 | 72.5 | 862.5 | 8 | D | III
E-CV2260077 | VCV | CV2III-350Y/40.5-10193W | CV2III-350Y/40.5-10193W | CV2III-600Y/40.5-10193W ¦ CM2III-500Y/72.5B-10193W ¦ CM2III-600Y/72.5B-10193W | exact |  | 278.9 | 40.5 | 862.5 | 8 | Y | III
E-CV2260078 | VCV | CV2III-350D/40.5-10070 | CV2III-350D/40.5-10070 | CV2III-600D/40.5-10070 ¦ CM2III-500D/72.5B-10070 ¦ CM2III-600D/72.5B-10070 | exact |  | 215 | 40.5 | 911.1 |  | D | III
E-CV2260079-082 | VCV | CV2III-350D/40.5-10193G | CV2III-350D/40.5-10193G | CV2III-600D/40.5-10193G ¦ CM2III-500D/72.5B-10193G ¦ CM2III-600D/72.5B-10193G | exact |  | 75.8 | 40.5 | 551 | 8 | D | III
E-CV2260083-085 | VCV | CV2III-350D/72.5-10193W |  |  | skip | no transformer I |  | 72.5 |  |  | D | III
E-CV2260086-087 | VCV | CV2III-350Y/40.5-10193W | CV2III-350Y/40.5-10193W | CV2III-600Y/40.5-10193W ¦ CM2III-500Y/72.5B-10193W ¦ CM2III-600Y/72.5B-10193W | exact |  | 209.18 | 40.5 | 431.25 | 8 | Y | III
E-CV2260088 | VCV |  |  |  | skip | no sold_type | 238 |  | 825
E-CV2260089-095 | VCV |  |  |  | skip | no sold_type |  |  | 1958 | 9
E-CV2260096-098 | VCV | CV2III-600D/40.5-10193G | CV2III-600D/40.5-10193G | CM2III-500D/72.5B-10193G ¦ CM2III-600D/72.5B-10193G ¦ SHZVIII-400D/72.5B-10193G | exact |  | 356 | 40.5 | 410 | 8 | D | III
E-CV2260099 | VCV | CV2III-350D/145-10193W | CV2III-350D/145-10193W | CV2III-600D/145-10193W ¦ CM2III-500D/170D-10193W ¦ CM2III-600D/170D-10193W | exact |  | 80.5 | 145 | 1725 | 8 | D | III
E-CV2260100 | VCV | CV2III-350Y/72.5-10191W | CV2III-350Y/72.5-10191W | CV2III-600Y/72.5-10191W ¦ CM2III-500Y/72.5B-10191W ¦ CM2III-600Y/72.5B-10191W | exact |  | 212 | 72.5 | 1184 | 9 | Y | III
E-CV2260101-103 | VCV | CV2III-600D/40.5-10193G | CV2III-600D/40.5-10193G | CM2III-500D/72.5B-10193G ¦ CM2III-600D/72.5B-10193G ¦ SHZVIII-600D/72.5B-10193G | exact |  | 442.8 | 40.5 | 412.5 | 8 | D | III
E-CV2260104 | VCV | CV2III-350Y/72.5-10191W | CV2III-350Y/72.5-10191W | CV2III-600Y/72.5-10191W ¦ CM2III-500Y/72.5B-10191W ¦ CM2III-600Y/72.5B-10191W | exact |  | 334 | 72.5 | 1184 | 9 | Y | III
E-CV2260105-106 | VCV | CV2III-350D/145-12231W | CV2III-350D/145-12231W | CV2III-600D/145-12231W ¦ CM2III-500D/170D-12231W ¦ CM2III-600D/170D-12231W | exact |  | 88.2 | 145 | 763.6 | 11 | D | III
E-CV2260105-106 | VCV | CV2III-350D/145-12231W | CV2III-350D/145-12231W | CV2III-600D/145-12231W ¦ CM2III-500D/170D-12231W ¦ CM2III-600D/170D-12231W | exact |  | 88.2 | 145 | 763.5 | 11 | D | III
E-CV2260107 | VCV | CV2III-350D/72.5-10193W | CV2III-350D/72.5-10193W | CV2III-600D/72.5-10193W ¦ CM2III-500D/72.5B-10193W ¦ CM2III-600D/72.5B-10193W | exact |  | 142.3 | 72.5 | 862.5 | 8 | D | III
E-CV2260108 | VCV | CV2III-350D/145-10193W | CV2III-350D/145-10193W | CV2III-600D/145-10193W ¦ CM2III-500D/170D-10193W ¦ CM2III-600D/170D-10193W | exact |  | 40.3 | 145 | 0 | 8 | D | III
E-CV2260109 | VCV | CV2III-350D/145-10193W | CV2III-350D/145-10193W | CV2III-600D/145-10193W ¦ CM2III-500D/170D-10193W ¦ CM2III-600D/170D-10193W | exact |  | 80.5 | 145 | 1725 | 8 | D | III
E-CV2260110 | VCV | CVIII-350Y/72.5-10193W | CV2III-350Y/72.5-10193W | CV2III-600Y/72.5-10193W ¦ CVIII-350Y/72.5-10193W ¦ SVIII-500Y/72.5-10193W | eligible |  | 213.8 | 72.5 | 0 | 8 | Y | III
E-CV2260111 | VCV | CV2III-350Y/72.5-10191W | CV2III-350Y/72.5-10191W | CV2III-600Y/72.5-10191W ¦ CM2III-500Y/72.5B-10191W ¦ CM2III-600Y/72.5B-10191W | exact |  | 212 | 72.5 | 1182 | 9 | Y | III
E-CV2260112 | VCV | CV2III-600D/126-10193W | CV2III-600D/126-10193W | CM2III-500D/126C-10193W ¦ CM2III-600D/126C-10193W ¦ SHZVIII-400D/126C-10193W | exact |  | 348.6 | 126 | 497.96 | 8 | D | III
E-CV2260113-114 | VCV | CV2III-350D/72.5-10193W | CV2III-350D/72.5-10193W | CV2III-600D/72.5-10193W ¦ CM2III-500D/72.5B-10193W ¦ CM2III-600D/72.5B-10193W | exact |  | 96.6 | 72.5 | 862.5 | 8 | D | III
E-CV2260115 | VCV | CV2III-350D/72.5-10193W | CV2III-350D/72.5-10193W | CV2III-600D/72.5-10193W ¦ CM2III-500D/72.5B-10193W ¦ CM2III-600D/72.5B-10193W | exact |  | 90.9 | 72.5 | 550 | 8 | D | III
E-CV2260116-117 | VCV | CV2III-350D/145-12233W | CM2III-500D/170D-12233W | CM2III-600D/170D-12233W ¦ SHZVIII-400D/170D-12233W ¦ SHZVIII-600D/170D-12233W | miss |  | 96.6 | 145 | 1725 | 10 | D | III | Ust 1725 V > CV2 12-pitch max 1500 V; CM2 covers. Sale slightly over brochure
E-CV2260118-119 | VCV | CV2III-600D/40.5-10193W | CV2III-600D/40.5-10193W | CM2III-600D/72.5B-10193W ¦ SHZVIII-600D/72.5B-10193W ¦ SHZVIII-1000D/72.5B-10193W | exact |  | 563 | 40.5 | 236.3 | 8 | D | III
E-CV2260120 | VCV | CV2III-350Y/72.5-10193W | CV2III-350Y/72.5-10193W | CV2III-600Y/72.5-10193W ¦ CM2III-500Y/72.5B-10193W ¦ CM2III-600Y/72.5B-10193W | exact |  | 167.3 | 72.5 | 996 | 8 | Y | III
E-CV2260121 | VCV | CV2III-350D/145-10193W | CV2III-350D/145-10193W | CV2III-600D/145-10193W ¦ CM2III-500D/170D-10193W ¦ CM2III-600D/170D-10193W | exact |  | 30.2 | 145 | 1725 | 8 | D | III
E-CV2260122 | VCV | CV2III-350Y/72.5-10193W | CV2III-350Y/72.5-10193W | CV2III-600Y/72.5-10193W ¦ CM2III-500Y/72.5B-10193W ¦ CM2III-600Y/72.5B-10193W | exact |  | 220.2 | 72.5 | 995.9 | 8 | Y | III
E-CV2260123-124 | VCV | CV2III-350D/145-10193W | CV2III-350D/145-10193W | CV2III-600D/145-10193W ¦ CM2III-500D/170D-10193W ¦ CM2III-600D/170D-10193W | exact |  | 80.44 | 145 | 1725 | 8 | D | III
E-CV2260125 | VCV | CV2III-350D/145-10193W | CV2III-350D/145-10193W | CV2III-600D/145-10193W ¦ CM2III-500D/170D-10193W ¦ CM2III-600D/170D-10193W | exact |  | 56.81 | 145 | 1725 | 8 | D | III
E-CV2260126 | VCV | CV2III-350Y/40.5-10193W | CV2III-350Y/40.5-10193W | CV2III-600Y/40.5-10193W ¦ CM2III-500Y/72.5B-10193W ¦ CM2III-600Y/72.5B-10193W | exact |  | 125.5 | 40.5 | 497.96 | 8 | Y | III
E-CV2260127-129 | VCV | CV2III-600Y/72.5-10191W | CV2III-600Y/72.5-10191W | CM2III-500Y/72.5B-10191W ¦ CM2III-600Y/72.5B-10191W ¦ SHZVIII-400Y/72.5B-10191W | exact |  | 352.2 | 72.5 | 1242.1 | 9 | Y | III
E-CV2260130 | VCV | CV2III-350D/145-10193W | CV2III-350D/145-10193W | CV2III-600D/145-10193W ¦ CM2III-500D/170D-10193W ¦ CM2III-600D/170D-10193W | exact |  | 47.1 | 145 | 1725 | 8 | D | III
E-CV2260131-132 | VCV |  |  |  | skip | no sold_type
E-CV2260133 | VCV | CV2III-350Y/72.5-10193W | CV2III-350Y/72.5-10193W | CV2III-600Y/72.5-10193W ¦ CM2III-500Y/72.5B-10193W ¦ CM2III-600Y/72.5B-10193W | exact |  | 209.2 | 72.5 | 996 | 8 | Y | III
E-CV2260134-135 | VCV |  |  |  | skip | no sold_type
E-CV2260136 | VCV | CV2III-350Y/72.5-10193W | CV2III-350Y/72.5-10193W | CV2III-600Y/72.5-10193W ¦ CM2III-500Y/72.5B-10193W ¦ CM2III-600Y/72.5B-10193W | exact |  | 209.2 | 72.5 | 996 | 8 | Y | III
E-CV2260137 | VCV | CV2III-350Y/40.5-10193W | CV2III-350Y/40.5-10193W | CV2III-600Y/40.5-10193W ¦ CM2III-500Y/72.5B-10193W ¦ CM2III-600Y/72.5B-10193W | exact |  | 104.6 | 40.5 | 431.25 | 8 | Y | III
E-CV2260139-145 | VCV | CV2III-600Y/72.5-12233G | CV2III-600Y/72.5-12233G | CM2III-500Y/72.5B-12233G ¦ CM2III-600Y/72.5B-12233G ¦ SHZVIII-400Y/72.5B-12233G | exact |  | 367 | 72.5 | 545 | 10 | Y | III
E-CV2260146-147 | VCV | CV2III-350Y/72.5-10191W | CV2III-350Y/72.5-10191W | CV2III-600Y/72.5-10191W ¦ CM2III-500Y/72.5B-10191W ¦ CM2III-600Y/72.5B-10191W | exact |  | 334.1 | 72.5 | 1182 | 9 | Y | III
E-CV2260148 | VCV | CV2III-350D/145-10193W | CV2III-350D/145-10193W | CV2III-600D/145-10193W ¦ CM2III-500D/170D-10193W ¦ CM2III-600D/170D-10193W | exact |  | 56.8 | 145 | 1725 | 8 | D | III
E-CV2260149-150 | VCV | CV2III-350D/145-10193W | CV2III-350D/145-10193W | CV2III-600D/145-10193W ¦ CM2III-500D/170D-10193W ¦ CM2III-600D/170D-10193W | exact |  | 113.68 | 145 | 1725 | 8 | D | III
E-CV2260151 | VCV | CV2III-350D/72.5-10193W | CV2III-350D/72.5-10193W | CV2III-600D/72.5-10193W ¦ CM2III-500D/72.5B-10193W ¦ CM2III-600D/72.5B-10193W | exact |  | 71.01 | 72.5 | 862.5 | 8 | D | III
E-CV2260152-155 | VCV | CV2III-350D/72.5-10193W | CV2III-350D/72.5-10193W | CV2III-600D/72.5-10193W ¦ CM2III-500D/72.5B-10193W ¦ CM2III-600D/72.5B-10193W | exact |  | 71.01 | 72.5 | 862.5 | 8 | D | III
E-CV2260156 | VCV | CV2III-350D/72.5-10193W | CV2III-350D/72.5-10193W | CV2III-600D/72.5-10193W ¦ CM2III-500D/72.5B-10193W ¦ CM2III-600D/72.5B-10193W | exact |  | 71.01 | 72.5 | 862.5 | 8 | D | III
E-CV2260157-159 | VCV | CV2III-600Y/72.5-10193G | CV2III-600Y/72.5-10193G | CM2III-500Y/72.5B-10193G ¦ CM2III-600Y/72.5B-10193G ¦ SHZVIII-600Y/72.5B-10193G | exact |  | 393.6 | 72.5 | 1270.2 | 8 | Y | III
E-CV2260160-161 | VCV |  |  |  | skip | no sold_type |  |  | 1958 | 9
E-CV2260162-164 | VCV | CV2III-600Y/72.5-10193G |  |  | skip | no transformer I |  | 72.5 |  |  | Y | III
E-CV2260165-166 | VCV | CV2III-600Y/72.5-10191W | CV2III-600Y/72.5-10191W | CM2III-500Y/72.5B-10191W ¦ CM2III-600Y/72.5B-10191W ¦ SHZVIII-400Y/72.5B-10191W | exact |  | 351 | 72.5 | 1182 | 9 | Y | III
E-CV2260167-169 | VCV | CV2III-350D/72.5-10193W | CV2III-350D/72.5-10193W | CV2III-600D/72.5-10193W ¦ CM2III-500D/72.5B-10193W ¦ CM2III-600D/72.5B-10193W | exact |  | 160.9 | 72.5 | 862.5 | 8 | D | III
E-CV2260170 | VCV | CV2III-350D/145-10193W |  |  | skip | no transformer I |  | 145 | 1725 |  | D | III
E-CV2260171 | VCV | CV2III-600Y/72.5-10191W | CV2III-600Y/72.5-10191W | CM2III-500Y/72.5B-10191W ¦ CM2III-600Y/72.5B-10191W ¦ SHZVIII-600Y/72.5B-10191W | exact |  | 432 | 72.5 | 606 | 9 | Y | III
E-CV2260172 | VCV |  |  |  | skip | no sold_type
E-CV2260173 | VCV | CV2III-350Y/72.5-10193W | CV2III-350Y/72.5-10193W | CV2III-600Y/72.5-10193W ¦ CM2III-500Y/72.5B-10193W ¦ CM2III-600Y/72.5B-10193W | exact |  | 205.83 | 72.5 | 476 | 8 | Y | III
E-CV2260174-176 | VCV | CV2III-350D/72.5-10193W | CV2III-350D/72.5-10193W | CV2III-600D/72.5-10193W ¦ CM2III-500D/72.5B-10193W ¦ CM2III-600D/72.5B-10193W | exact |  | 71.01 | 72.5 | 862.5 | 8 | D | III
E-CV2260177-178 | VCV | CV2III-350D/72.5-10193W | CV2III-350D/72.5-10193W | CV2III-600D/72.5-10193W ¦ CM2III-500D/72.5B-10193W ¦ CM2III-600D/72.5B-10193W | exact |  | 71 | 72.5 | 862.5 | 8 | D | III
E-CV2260179-180 | VCV | CV2III-350D/72.5-10193W | CV2III-350D/72.5-10193W | CV2III-600D/72.5-10193W ¦ CM2III-500D/72.5B-10193W ¦ CM2III-600D/72.5B-10193W | exact |  | 268.3 | 72.5 | 862.5 | 8 | D | III
E-CV2260181-182 | VCV | CV2III-350D/145-10193W | CV2III-350D/145-10193W | CV2III-600D/145-10193W ¦ CM2III-500D/170D-10193W ¦ CM2III-600D/170D-10193W | exact |  | 161 | 145 | 1725 | 8 | D | III
E-CV2260183-184 | VCV | CV2III-600Y/72.5-10193W | CV2III-600Y/72.5-10193W | CM2III-500Y/72.5B-10193W ¦ CM2III-600Y/72.5B-10193W ¦ SHZVIII-600Y/72.5B-10193W | exact |  | 464.9 | 72.5 | 862.5 | 8 | Y | III
E-CV2260185 | VCV | CV2III-350D/145-10193W | CV2III-350D/145-10193W | CV2III-600D/145-10193W ¦ CM2III-500D/170D-10193W ¦ CM2III-600D/170D-10193W | exact |  | 85.3 | 145 | 1725 | 8 | D | III
E-CV2260186-187 | VCV | CV2III-350D/145-10193W | CV2III-350D/145-10193W | CV2III-600D/145-10193W ¦ CM2III-500D/170D-10193W ¦ CM2III-600D/170D-10193W | exact |  | 42.6 | 145 | 1725 | 8 | D | III
E-CV2260188 | VCV | CV2III-350D/145-10193W | CV2III-350D/145-10193W | CV2III-600D/145-10193W ¦ CM2III-500D/170D-10193W ¦ CM2III-600D/170D-10193W | exact |  | 40.3 | 145 | 1725 | 8 | D | III
E-CV2260189-190 | VCV | CV2III-350D/72.5-10193W | CV2III-350D/72.5-10193W | CV2III-600D/72.5-10193W ¦ CM2III-500D/72.5B-10193W ¦ CM2III-600D/72.5B-10193W | exact |  | 80.51 | 72.5 | 862.5 | 8 | D | III
E-CV2260191-193 | VCV | CV2III-350D/72.5-10193W | CV2III-350D/72.5-10193W | CV2III-600D/72.5-10193W ¦ CM2III-500D/72.5B-10193W ¦ CM2III-600D/72.5B-10193W | exact |  | 71.01 | 72.5 | 862.5 | 8 | D | III
E-CV2260194 | VCV | CV2III-350D/72.5-10193W | CV2III-350D/72.5-10193W | CV2III-600D/72.5-10193W ¦ CM2III-500D/72.5B-10193W ¦ CM2III-600D/72.5B-10193W | exact |  | 71 | 72.5 | 862.5 | 8 | D | III
E-CV2260195 | VCV | CV2III-350D/145-10193W | CV2III-350D/145-10193W | CV2III-600D/145-10193W ¦ CM2III-500D/170D-10193W ¦ CM2III-600D/170D-10193W | exact |  | 72.46 | 145 | 1725 | 8 | D | III
E-CV2260196 | VCV | CV2III-350D/145-12231W | CV2III-350D/145-12231W | CV2III-600D/145-12231W ¦ CM2III-500D/170D-12231W ¦ CM2III-600D/170D-12231W | exact |  | 40.3 | 145 | 1254.5 | 11 | D | III
E-CV2260197 | VCV |  |  |  | skip | no sold_type
E-CV2260198 | VCV | CV2III-350Y/72.5-10193W | CV2III-350Y/72.5-10193W | CV2III-600Y/72.5-10193W ¦ CM2III-500Y/72.5B-10193W ¦ CM2III-600Y/72.5B-10193W | exact |  | 167.3 | 72.5 | 996 | 8 | Y | III
E-CV2260199-202 | VCV | CV2III-350D/72.5-10193W | CV2III-350D/72.5-10193W | CV2III-600D/72.5-10193W ¦ CM2III-500D/72.5B-10193W ¦ CM2III-600D/72.5B-10193W | exact |  | 60.4 | 72.5 | 862.5 | 8 | D | III
E-CV2260203 | VCV | CV2III-350Y/72.5-10191W | CV2III-350Y/72.5-10191W | CV2III-600Y/72.5-10191W ¦ CM2III-500Y/72.5B-10191W ¦ CM2III-600Y/72.5B-10191W | exact |  | 334 | 72.5 | 0 | 9 | Y | III
E-CV2260204 | VCV | CV2III-350D/72.5-10193W | CV2III-350D/72.5-10193W | CV2III-600D/72.5-10193W ¦ CM2III-500D/72.5B-10193W ¦ CM2III-600D/72.5B-10193W | exact |  | 60.39 | 72.5 | 862.5 | 8 | D | III
E-CV2260205-210 | VCV |  |  |  | skip | no sold_type |  |  | 1958 | 9
E-CV2260211 | VCV | CV2III-350D/72.5-10193W | CV2III-350D/72.5-10193W | CV2III-600D/72.5-10193W ¦ CM2III-500D/72.5B-10193W ¦ CM2III-600D/72.5B-10193W | exact |  | 60.39 | 72.5 | 862.5 | 8 | D | III
E-CV2260212 | VCV | CV2III-350D/72.5-10193W |  |  | skip | no transformer I |  | 72.5 |  |  | D | III
E-CV2260213 | VCV | CV2III-350D/40.5-10100 | CV2III-350D/40.5-10100 | CV2III-600D/40.5-10100 ¦ CM2III-500D/72.5B-10100 ¦ CM2III-600D/72.5B-10100 | exact |  | 9.4 | 40.5 | 825 |  | D | III
E-CV2260214 | VCV | CV2III-350D/40.5-10193W | CV2III-350D/40.5-10193W | CV2III-600D/40.5-10193W ¦ CM2III-500D/72.5B-10193W ¦ CM2III-600D/72.5B-10193W | exact |  | 241.9 | 40.5 | 544.5 | 8 | D | III
E-CV2260215-216 | VCV | CV2III-600Y/72.5-10193W | CV2III-600Y/72.5-10193W | CM2III-600Y/72.5B-10193W ¦ SHZVIII-600Y/72.5B-10193W ¦ SHZVIII-1000Y/72.5B-10193W | exact |  | 570.2 | 72.5 | 0 | 8 | Y | III
E-CV2260217 | VCV | CV2III-350D/145-10193W | CV2III-350D/145-10193W | CV2III-600D/145-10193W ¦ CM2III-500D/170D-10193W ¦ CM2III-600D/170D-10193W | exact |  | 64.26 | 145 | 1725 | 8 | D | III
E-CV2260218 | VCV | CV2III-350D/72.5-10193W | CV2III-350D/72.5-10193W | CV2III-600D/72.5-10193W ¦ CM2III-500D/72.5B-10193W ¦ CM2III-600D/72.5B-10193W | exact |  | 120.8 | 72.5 | 862.5 | 8 | D | III
E-CV2260219 | VCV | CV2III-600Y/72.5-10193W | CV2III-600Y/72.5-10193W | CM2III-500Y/72.5B-10193W ¦ CM2III-600Y/72.5B-10193W ¦ SHZVIII-600Y/72.5B-10193W | exact |  | 393.6 | 72.5 | 1270.2 | 8 | Y | III
E-CV2260220 | VCV | CV2III-350D/145-10193W | CV2III-350D/145-10193W | CV2III-600D/145-10193W ¦ CM2III-500D/170D-10193W ¦ CM2III-600D/170D-10193W | exact |  | 96.62 | 145 | 1725 | 8 | D | III
E-CV2260221 | VCV |  |  |  | skip | no sold_type | 144.1 |  | 476.3
E-CV2260222-223 | VCV | CV2III-350Y/72.5-10191W |  |  | skip | no transformer I |  | 72.5 |  |  | Y | III
E-CV2260224 | VCV | CV2III-350Y/72.5-10191W |  |  | skip | no transformer I |  | 72.5 |  |  | Y | III
E-CV2260225 | VCV | CV2III-350D/145-10193W | CV2III-350D/145-10193W | CV2III-600D/145-10193W ¦ CM2III-500D/170D-10193W ¦ CM2III-600D/170D-10193W | exact |  | 75.6 | 145 | 1725 | 8 | D | III
E-CV2260226 | VCV | CV2III-350D/72.5-10193 |  |  | skip | no transformer I |  | 72.5 | 862.5 |  | D | III
E-CV2260227-229 | VCV | CV2III-350D/40.5-10193W | CV2III-350D/40.5-10193W | CV2III-600D/40.5-10193W ¦ CM2III-500D/72.5B-10193W ¦ CM2III-600D/72.5B-10193W | exact |  | 72.46 | 40.5 | 431.25 | 8 | D | III
E-CV2260230 | VCV | CV2III-350D/145-10193W | CV2III-350D/145-10193W | CV2III-600D/145-10193W ¦ CM2III-500D/170D-10193W ¦ CM2III-600D/170D-10193W | exact |  | 15.1 | 145 | 1725 | 8 | D | III
E-CV2260231-235 | VCV | CV2III-350D/72.5-10193W | CV2III-350D/72.5-10193W | CV2III-600D/72.5-10193W ¦ CM2III-500D/72.5B-10193W ¦ CM2III-600D/72.5B-10193W | exact |  | 128.5 | 72.5 | 862.5 | 8 | D | III
E-CV2260236-237 | VCV | CV2III-350D/72.5-10193W | CV2III-350D/72.5-10193W | CV2III-600D/72.5-10193W ¦ CM2III-500D/72.5B-10193W ¦ CM2III-600D/72.5B-10193W | exact |  | 60.38 | 72.5 | 863 | 8 | D | III
E-CV2260238-239 | VCV | CV2III-350D/40.5-12233W | CV2III-350D/40.5-12233W | CV2III-600D/40.5-12233W ¦ CM2III-500D/72.5B-12233W ¦ CM2III-600D/72.5B-12233W | exact |  | 148 | 40.5 | 0 | 10 | D | III
E-CV2260240-241 | VCV | CV2III-350Y/72.5-10193W | CV2III-350Y/72.5-10193W | CV2III-600Y/72.5-10193W ¦ CM2III-500Y/72.5B-10193W ¦ CM2III-600Y/72.5B-10193W | exact |  | 268 | 72.5 | 318 | 8 | Y | III
E-CV2260242-243 | VCV | CV2III-350Y/72.5-10191W | CV2III-350Y/72.5-10191W | CV2III-600Y/72.5-10191W ¦ CM2III-500Y/72.5B-10191W ¦ CM2III-600Y/72.5B-10191W | exact |  | 133 | 72.5 | 1182 | 9 | Y | III
E-CV2260244 | VCV | CV2III-350Y/72.5-10191W |  |  | skip | no transformer I |  | 72.5 |  |  | Y | III
E-CV2260245-246 | VCV | CV2III-600Y/40.5-10193W | CV2III-600Y/40.5-10193W | CM2III-500Y/72.5B-10193W ¦ CM2III-600Y/72.5B-10193W ¦ SHZVIII-400Y/72.5B-10193W | exact |  | 347.1 | 40.5 | 733.3 | 8 | Y | III
E-CV2260247 | VCV | CV2III-600D/40.5-12110 | CV2III-600D/40.5-12110 | CM2III-500D/72.5B-12110 ¦ CM2III-600D/72.5B-12110 ¦ SHZVIII-400D/72.5B-12110 | exact |  | 377.1 | 40.5 | 437.5 |  | D | III
E-CV2260248-249 | VCV | CV2III-600D/72.5-10193G |  |  | skip | no transformer I |  | 72.5 |  |  | D | III
E-CV2260250 | VCV | CV2III-350Y/72.5-10191W | CV2III-350Y/72.5-10191W | CV2III-600Y/72.5-10191W ¦ CM2III-500Y/72.5B-10191W ¦ CM2III-600Y/72.5B-10191W | exact |  | 142.1 | 72.5 | 1243.5 | 9 | Y | III
E-CV2260251 | VCV | CV2III-350Y/40.5-10193W |  |  | skip | no transformer I |  | 40.5 |  |  | Y | III
E-CV2260252 | VCV | CV2III-500Y/72.5-10191W |  |  | skip | no transformer I |  | 72.5 |  |  | Y | III
E-CV2260253 | VCV | CV2III-350Y/72.5-10191G | CV2III-350Y/72.5-10191G | CV2III-600Y/72.5-10191G ¦ CM2III-500Y/72.5B-10191G ¦ CM2III-600Y/72.5B-10191G | exact |  | 270 | 72.5 | 607 | 9 | Y | III
E-CV2260254-256 | VCV | CV2III-350D/72.5-10193W | CV2III-350D/72.5-10193W | CV2III-600D/72.5-10193W ¦ CM2III-500D/72.5B-10193W ¦ CM2III-600D/72.5B-10193W | exact |  | 71 | 72.5 | 862.5 | 8 | D | III
E-CV2260257 | VCV | CV2III-350D/72.5-10193W | CV2III-350D/72.5-10193W | CV2III-600D/72.5-10193W ¦ CM2III-500D/72.5B-10193W ¦ CM2III-600D/72.5B-10193W | exact |  | 151.21 | 72.5 | 862.5 | 8 | D | III
E-CV2260258 | VCV | CV2III-350D/72.5-10193W | CV2III-350D/72.5-10193W | CV2III-600D/72.5-10193W ¦ CM2III-500D/72.5B-10193W ¦ CM2III-600D/72.5B-10193W | exact |  | 151.21 | 72.5 | 862.5 | 8 | D | III
E-CV2260259-262 | VCV | CV2III-350D/145-10193W | CV2III-350D/145-10193W | CV2III-600D/145-10193W ¦ CM2III-500D/170D-10193W ¦ CM2III-600D/170D-10193W | exact |  | 64.26 | 145 | 1725 | 8 | D | III
E-CV2260263 | VCV | CV2III-350D/145-10193W | CV2III-350D/145-10193W | CV2III-600D/145-10193W ¦ CM2III-500D/170D-10193W ¦ CM2III-600D/170D-10193W | exact |  | 72.46 | 145 | 1725 | 8 | D | III
E-CV2260264-265 | VCV | CV2III-350D/145-10193W | CV2III-350D/145-10193W | CV2III-600D/145-10193W ¦ CM2III-500D/170D-10193W ¦ CM2III-600D/170D-10193W | exact |  | 75.58 | 145 | 1725 | 8 | D | III
E-CV2260266-267 | VCV | CV2III-600D/72.5-10193G |  |  | skip | no transformer I |  | 72.5 |  |  | D | III
E-CV2260268 | VCV | CV2III-350D/40.5-10091W | CV2III-350D/40.5-10091W | CV2III-600D/40.5-10091W ¦ CM2III-500D/72.5B-10091W ¦ CM2III-600D/72.5B-10091W | exact |  | 181.2 | 40.5 | 359 | 4 | D | III
E-CV2260269 | VCV | CV2III-350Y/72.5-10191W | CV2III-350Y/72.5-10191W | CV2III-600Y/72.5-10191W ¦ CM2III-500Y/72.5B-10191W ¦ CM2III-600Y/72.5B-10191W | exact |  | 84.9 | 72.5 | 0 | 9 | Y | III
E-CV2260270-271 | VCV | CV2III-350Y/72.5-10193W | CV2III-350Y/72.5-10193W | CV2III-600Y/72.5-10193W ¦ CM2III-500Y/72.5B-10193W ¦ CM2III-600Y/72.5B-10193W | exact |  | 24.5 | 72.5 | 1368 | 8 | Y | III
E-CV2260272-274 | VCV | CV2III-350D/145-10193W | CV2III-350D/145-10193W | CV2III-600D/145-10193W ¦ CM2III-500D/170D-10193W ¦ CM2III-600D/170D-10193W | exact |  | 130.9 | 145 | 996 | 8 | D | III
E-CV2260275-276 | VCV | CV2III-350D/145-10193W | CV2III-350D/145-10193W | CV2III-600D/145-10193W ¦ CM2III-500D/170D-10193W ¦ CM2III-600D/170D-10193W | exact |  | 64.26 | 145 | 1725 | 8 | D | III
E-CV2260277 | VCV | CV2III-600D/72.5-12233W | SHZVIII-1000D/72.5B-12233W | SHZVGIII-1300D/72.5B-12233W ¦ SHZVGIII-1500D/72.5B-12233W ¦ 3xCM2I-800/72.5B-12233W | miss |  | 603.75 | 72.5 | 0 | 10 | D | III | I=603.75 > CV2 III 600; engine steps to SHZV-1000. Borderline oversize
E-CV2260278 | VCV | CV2III-600Y/72.5-10193W | CV2III-600Y/72.5-10193W | CM2III-500Y/72.5B-10193W ¦ CM2III-600Y/72.5B-10193W ¦ SHZVIII-400Y/72.5B-10193W | exact |  | 376.53 | 72.5 | 1725 | 8 | Y | III
E-CV2260279-280 | VCV | CV2III-350D/72.5-10193W | CV2III-350D/72.5-10193W | CV2III-600D/72.5-10193W ¦ CM2III-500D/72.5B-10193W ¦ CM2III-600D/72.5B-10193W | exact |  | 160.9 | 72.5 | 862.5 | 8 | D | III
E-CV2260281 | VCV | CV2III-600D/72.5-10193G |  |  | skip | no transformer I |  | 72.5 |  |  | D | III
E-CV2260282-283 | VCV | CV2III-600D/72.5-10193G |  |  | skip | no transformer I |  | 72.5 |  |  | D | III
E-CV2260284 | VCV | CV2III-600D/40.5-12233W |  |  | skip | no transformer I |  | 40.5 |  |  | D | III
E-CV2260285 | VCV | CV2III-350D/40.5-10193W | CV2III-350D/40.5-10193W | CV2III-600D/40.5-10193W ¦ CM2III-500D/72.5B-10193W ¦ CM2III-600D/72.5B-10193W | exact |  | 72.46 | 40.5 | 431.25 | 8 | D | III
E-CV2260286 | VCV | CV2III-600D/40.5-10091W |  |  | skip | no transformer I |  | 40.5 |  |  | D | III
E-CV2260287 | VCV | CV2III-350D/145-10193W | CV2III-350D/145-10193W | CV2III-600D/145-10193W ¦ CM2III-500D/170D-10193W ¦ CM2III-600D/170D-10193W | exact |  | 72.46 | 145 | 1725 | 8 | D | III
E-CV2260288 | VCV | CV2III-600D/40.5-10193W |  |  | skip | no transformer I |  | 40.5 |  |  | D | III
E-CV2260289 | VCV | CV2III-350D/145-10193W | CV2III-350D/145-10193W | CV2III-600D/145-10193W ¦ CM2III-500D/170D-10193W ¦ CM2III-600D/170D-10193W | exact |  | 62.76 | 145 | 0 | 8 | D | III
E-CV2260290-291 | VCV | CV2III-600Y/72.5-10193W | CV2III-600Y/72.5-10193W | CM2III-600Y/72.5B-10193W ¦ SHZVIII-600Y/72.5B-10193W ¦ SHZVIII-1000Y/72.5B-10193W | exact |  | 535 | 72.5 | 318 | 8 | Y | III
E-CV2260292-293 | VCV | CV2III-600D/72.5-10193G |  |  | skip | no transformer I |  | 72.5 |  |  | D | III
E-CV2260294-295 | VCV | CV2III-600D/72.5-10193G |  |  | skip | no transformer I |  | 72.5 |  |  | D | III
E-CV2260296 | VCV | CV2III-600D/126-10193W | CV2III-600D/126-10193W | CM2III-500D/126C-10193W ¦ CM2III-600D/126C-10193W ¦ SHZVIII-600D/126C-10193W | exact |  | 411.66 | 126 | 952.63 | 8 | D | III
E-CV2260297 | VCV | CV2III-600D/725-10193W |  |  | miss | Parameters out of catalogue range (current, Um, step voltage, or positions). | 411.66 | 725 | 952.63 | 8 | D | III | Um parsed 725 (72.5 glued). Data error
E-CV2260298 | VCV | CV2III-350D/72.5-12233W | CV2III-350D/72.5-12233W | CV2III-600D/72.5-12233W ¦ CM2III-500D/72.5B-12233W ¦ CM2III-600D/72.5B-12233W | exact |  | 133.27 | 72.5 | 897 | 10 | D | III
E-CV2260299-304 | VCV | CV2III-600Y/72.5-10191W |  |  | skip | no transformer I |  | 72.5 |  |  | Y | III
E-CV2260305-307 | VCV | CV2III-350D/72.5-10193W | CV2III-350D/72.5-10193W | CV2III-600D/72.5-10193W ¦ CM2III-500D/72.5B-10193W ¦ CM2III-600D/72.5B-10193W | exact |  | 196.9 | 72.5 | 498 | 8 | D | III
E-CV2260308 | VCV | CV2III-350D/145-10193W | CV2III-350D/145-10193W | CV2III-600D/145-10193W ¦ CM2III-500D/170D-10193W ¦ CM2III-600D/170D-10193W | exact |  | 64.26 | 145 | 1725 | 8 | D | III
E-CV2260309-312 | VCV | CV2III-350D/145-10193W | CV2III-350D/145-10193W | CV2III-600D/145-10193W ¦ CM2III-500D/170D-10193W ¦ CM2III-600D/170D-10193W | exact |  | 80.43 | 145 | 1725 | 8 | D | III
E-CV2260313 | VCV | CV2III-350Y/40.5-10193G | CV2III-350Y/40.5-10193G | CV2III-600Y/40.5-10193G ¦ CM2III-500Y/72.5B-10193G ¦ CM2III-600Y/72.5B-10193G | exact |  | 277.6 | 40.5 | 150 | 8 | Y | III
E-CV2260314 | VCV | CV2III-350D/40.5-10100 | CV2III-350D/40.5-10100 | CV2III-600D/40.5-10100 ¦ CM2III-500D/72.5B-10100 ¦ CM2III-600D/72.5B-10100 | exact |  | 241.6 | 40.5 | 910 |  | D | III
E-CV2260315-316 | VCV | CV2III-350Y/72.5-10191W | CV2III-350Y/72.5-10191W | CV2III-600Y/72.5-10191W ¦ CM2III-500Y/72.5B-10191W ¦ CM2III-600Y/72.5B-10191W | exact |  | 212 | 72.5 | 1182 | 9 | Y | III
E-CV2260317-318 | VCV | CV2III-350D/145-10193W | CV2III-350D/145-10193W | CV2III-600D/145-10193W ¦ CM2III-500D/170D-10193W ¦ CM2III-600D/170D-10193W | exact |  | 71 | 145 | 1725 | 8 | D | III
E-CV2260319-320 | VCV | CV2III-350D/72.5-10193W | CV2III-350D/72.5-10193W | CV2III-600D/72.5-10193W ¦ CM2III-500D/72.5B-10193W ¦ CM2III-600D/72.5B-10193W | exact |  | 196.9 | 72.5 | 498 | 8 | D | III
E-CV2260321 | VCV | CV2III-350D/126-10193W | CV2III-350D/126-10193W | CV2III-600D/126-10193W ¦ CM2III-500D/126C-10193W ¦ CM2III-600D/126C-10193W | exact |  | 263 | 126 | 0 | 8 | D | III
E-CV2260322-325 | VCV | CV2III-600Y/72.5-10191W | CV2III-600Y/72.5-10191W | CM2III-500Y/72.5B-10191W ¦ CM2III-600Y/72.5B-10191W ¦ SHZVIII-600Y/72.5B-10191W | exact |  | 458.2 | 72.5 | 606.3 | 9 | Y | III
E-CV2260326 | VCV |  |  |  | skip | no sold_type
E-CV2260327 | VCV | CV2III-350Y/72.5-10191W | CV2III-350Y/72.5-10191W | CV2III-600Y/72.5-10191W ¦ CM2III-500Y/72.5B-10191W ¦ CM2III-600Y/72.5B-10191W | exact |  | 257.3 | 72.5 | 1271 | 9 | Y | III
E-CV2260328 | VCV |  |  |  | skip | no sold_type
E-CV2260329-334 | VCV | CV2III-350D/40.5-10193W |  |  | skip | no transformer I |  | 40.5 |  |  | D | III
E-CV2260335-336 | VCV | CV2III-350D/145-12231W | CV2III-350D/145-12231W | CV2III-600D/145-12231W ¦ CM2III-500D/170D-12231W ¦ CM2III-600D/170D-12231W | exact |  | 252 | 145 | 763.6 | 11 | D | III
E-CV2260337 | VCV | CV2III-350D/145-12231W | CV2III-350D/145-12231W | CV2III-600D/145-12231W ¦ CM2III-500D/170D-12231W ¦ CM2III-600D/170D-12231W | exact |  | 116.2 | 145 | 1255 | 11 | D | III
E-CV2260338 | VCV | CV2III-350D/72.5-12231W | CV2III-350D/72.5-12231W | CV2III-600D/72.5-12231W ¦ CM2III-500D/72.5B-12231W ¦ CM2III-600D/72.5B-12231W | exact |  | 185.9 | 72.5 | 627.5 | 11 | D | III
E-CV2260339 | VCV | CV2III-500Y/72.5-10193W |  |  | skip | no transformer I |  | 72.5 |  |  | Y | III
E-CV2260340 | VCV | CV2III-350D/72.5-12231W | CV2III-350D/72.5-12231W | CV2III-600D/72.5-12231W ¦ CM2III-500D/72.5B-12231W ¦ CM2III-600D/72.5B-12231W | exact |  | 185.9 | 72.5 | 627.5 | 11 | D | III
E-CV2260341-342 | VCV | CV2III-600D/40.5-10193W | CV2III-600D/40.5-10193W | CM2III-500D/72.5B-10193W ¦ CM2III-600D/72.5B-10193W ¦ SHZVIII-600D/72.5B-10193W | exact |  | 438 | 40.5 | 275 | 8 | D | III
E-CV2260343-344 | VCV | CV2III-350D/40.5-10193W | CV2III-350D/40.5-10193W | CV2III-600D/40.5-10193W ¦ CM2III-500D/72.5B-10193W ¦ CM2III-600D/72.5B-10193W | exact |  | 168 | 40.5 | 275 | 8 | D | III
E-CV2260345 | VCV | CV2III-350D/145-10193W | CV2III-350D/145-10193W | CV2III-600D/145-10193W ¦ CM2III-500D/170D-10193W ¦ CM2III-600D/170D-10193W | exact |  | 64.26 | 145 | 1725 | 8 | D | III
E-CV2260346 | VCV | CV2III-600Y/72.5-10173G | CV2III-600Y/72.5-16151G | CM2III-500Y/72.5B-16151G ¦ CM2III-600Y/72.5B-16151G ¦ SHZVIII-600Y/72.5B-16151G | family-i-um |  | 419.6 | 72.5 | 739 | 7 | Y | III
E-CV2260349 | VCV |  |  |  | skip | no sold_type
E-WG260001 | WG | WDGV-800Y/40.5-6x5 |  |  | skip | unparsed sold_type |  | 40.5 | 555.7 |  | Y | V
E-WG260002-003 | WG | WDGV-800/40.5-6x5B |  |  | skip | unparsed sold_type |  | 40.5 | 555.7 |  |  | V
E-WG260004-009 | WG | WDGIV-800/40.5-5x5A |  |  | skip | unparsed sold_type | 631 | 40.5 |  | 2 |  | IV
E-WG260010-012 | WG | 3xWDGIV-400/40.5-5x5A |  |  | skip | unparsed sold_type | 394.6 | 40.5 |  | 2 |  | IV
E-WG260013-014 | WG | WDGV-800Y/40.5-6x5 |  |  | skip | unparsed sold_type |  | 40.5 | 555.7 |  | Y | V
E-WG260015-016 | WG | 3xWDGIV-400/72.5-5x5A |  |  | skip | unparsed sold_type | 395 | 72.5 |  | 2 |  | IV
E-WG260017-018 | WG | 3xWDGIV-400/40.5-5x5A |  |  | skip | unparsed sold_type | 394.6 | 40.5 |  | 2 |  | IV
E-WG260019 | WG | 3xWDGIV-800/72.5-5x5A |  |  | skip | unparsed sold_type | 630.6 | 72.5 |  | 2 |  | IV
E-WG260020 | WG | 3xWDGIV-400/72.5-5x5A |  |  | skip | unparsed sold_type | 395 | 72.5 |  | 2 |  | IV
E-WG260021-022 | WG | 3xWDGIV-400/72.5-5x5A |  |  | skip | unparsed sold_type | 395 | 72.5 |  | 2 |  | IV
E-WG260023 | WG | WDGV-800/40.5-6x5 |  |  | skip | unparsed sold_type |  | 40.5 |  |  |  | V
E-WG260024-026 | WG | WDGIV-800/40.5-5x5A |  |  | skip | unparsed sold_type | 631 | 40.5 |  | 2 |  | IV
E-WG260027 | WG | 3xWDGIV-400/72.5-5x5A |  |  | skip | unparsed sold_type | 395 | 72.5 |  | 2 |  | IV
E-WG260028-030 | WG |  |  |  | skip | no sold_type |  |  |  | 1
E-WG260031-032 | WG | CVIII-350Y/72.5-10191W | CV2III-350Y/72.5-10191W | CV2III-600Y/72.5-10191W ¦ CVIII-350Y/72.5-10191W ¦ SVIII-500Y/72.5-10191W | eligible |  | 252.6 | 72.5 | 0 | 9 | Y | III
E-WG260033 | WG |  |  |  | skip | no sold_type
E-WG260034 | WG | 3xWDGV-800/72.5-6x5B |  |  | skip | unparsed sold_type | 627.8 | 72.5 |  | 2 |  | V
E-WG260035-040 | WG | WDGIV-800/40.5-5x5A |  |  | skip | unparsed sold_type | 631 | 40.5 |  | 2 |  | IV
E-WG260041 | WG | 3xWDGIV-400/72.5-5x5A |  |  | skip | unparsed sold_type | 395 | 72.5 |  | 2 |  | IV
E-WG260042-043 | WG | 3xWDGIV-800/72.5-5x5A |  |  | skip | unparsed sold_type | 630.6 | 72.5 |  | 2 |  | IV
E-WG260044 | WG | 3xWDGIV-1250/72.5-5x5A |  |  | skip | unparsed sold_type | 995 | 72.5 |  | 2 |  | IV
E-WG260045 | WG | 3xWDGIV-400/40.5-5x5A |  |  | skip | unparsed sold_type | 394.6 | 40.5 |  | 2 |  | IV
E-W260001 | WL | WSLIV-600D/72.5-6x5B | WSLII-600D/72.5-12x11B | WSLII-800D/72.5-12x11B | family |  | 297 | 72.5 | 0 | 4 | D | III
E-W260002 | WL | WSLIV-600Y/72.5-6x5B | WSLIV-600Y/72.5-12x11B | WSLIV-800Y/72.5-12x11B | family-i-um |  | 515 | 72.5 | 0 | 4 | Y | III
E-W260003 | WL | WSLIV-600Y/72.5-6x5A | WSLIV-600Y/72.5-6x5A | WSLIV-800Y/72.5-6x5A | exact |  | 132.2 | 72.5 | 0 | 2 | Y | III
E-W260004-006 | WL | WSLIV-600Y/72.5-6x5A |  |  | skip | no transformer I |  | 72.5 |  |  | Y | IV
E-W260007 | WL | WSLIV-800Y/170-6x5B | WSLIV-800Y/170-6x5B | WSLIV-1000Y/170-6x5B | exact |  | 592.81 | 170 | 0 | 2 | Y | III
E-W260008-009 | WL | WDLIV-600/72.5-17x16E |  |  | miss | Parameters out of catalogue range (current, Um, step voltage, or positions). | 150 | 72.5 | 0 | 16 | Y | III | OCTC contact 17x16 not in 6x5/7x6/12x11/18x17
E-W260010 | WL | WSLIV-800Y/72.5-6x5A | WSLIV-800Y/72.5-6x5A | WSLIV-1000Y/72.5-6x5A | exact |  | 631.4 | 72.5 | 0 | 2 | Y | III
E-W260011 | WL | WSLIV-1600Y/72.5-6x5 | WSLIV-1200Y/72.5-6x5A | WSLIV-1600Y/72.5-6x5A | family |  | 994.5 | 72.5 | 0 | 2 | Y | III
E-W260012 | WL | WSLII-2000Y/72.5-6x5B | WSLIV-1600Y/72.5-6x5A | WSLIV-2000Y/72.5-6x5A | family |  | 1323 | 72.5 | 332 | 2 | Y | II
E-W260013 | WL | WSLII-2000Y/72.5-6x5B | WSLIV-600Y/72.5-6x5A | WSLIV-800Y/72.5-6x5A | family |  | 212 | 72.5 | 3320 | 2 | Y | II
E-W260014-015 | WL | WSLIV-800D/72.5-6x5A | WSLII-800D/72.5-6x5A | WSLII-1000D/72.5-6x5A | family |  | 637.9 | 72.5 | 550 | 2 | D | III
E-W260016-017 | WL |  |  |  | skip | no sold_type
E-W260018 | WL |  |  |  | skip | no sold_type
E-W260019 | WL | CMIII-600Y/72.5C-14271G |  |  | skip | no transformer I |  | 72.5 |  |  | Y | III
E-W260020 | WL | WSLII-800D/72.5-6x5A |  |  | skip | no transformer I |  | 72.5 |  |  | D | II
E-W260021 | WL |  |  |  | skip | no sold_type | 303
E-W260022-023 | WL | WDLIV-1200/72.5-9x8E | WSLIV-1000Y/72.5-18x17E | WSLIV-1200Y/72.5-18x17E | miss |  | 1000 | 72.5 | 0 | 8 | Y | III | OCTC contact 9x8 not catalogue; nearest 18x17
E-W260024-025 | WL |  |  |  | skip | no sold_type | 600
E-W260026-027 | WL |  |  |  | skip | no sold_type
E-W260028 | WL | WSLIV-600D/72.5-6x5A | WSLII-600D/72.5-6x5A | WSLII-800D/72.5-6x5A | family |  | 255.2 | 72.5 | 550 | 2 | D | III
E-W260029 | WL |  |  |  | skip | no sold_type
E-W260030-031 | WL | WSLV-800D/126-6x5A | WSLII-800D/126-6x5B | WSLII-1000D/126-6x5B | family |  | 627.8 | 126 | 0 | 2 | D | III
E-W260032,E-W260037 | WL |  |  |  | skip | no sold_type
E-W260033-034 | WL | WSLII-800D/72.5-6x5A |  |  | skip | no transformer I |  | 72.5 |  |  | D | II
E-W260035 | WL | WSLII-600D/72.5-12x11C | WSLII-600D/72.5-12x11B | WSLII-800D/72.5-12x11B | family-i-um |  | 185 | 72.5 | 1675 | 5 | D | II
E-W260036 | WL | WSLIV-600D/72.5-6x5A | WSLII-600D/72.5-6x5A | WSLII-800D/72.5-6x5A | family |  | 255.2 | 72.5 | 550 | 2 | D | III
E-W260038 | WL | WSLIV-600Y/72.5-6x5A | WSLIV-600Y/72.5-6x5A | WSLIV-800Y/72.5-6x5A | exact |  | 395 | 72.5 | 0 | 2 | Y | III
E-W260039 | WL | WSLIV-1600D/72.5-7x6D | WSLII-1600D/72.5-18x17E | WSLII-2000D/72.5-18x17E | family |  | 1217.4 | 72.5 | 0 | 7 | D | III
E-W260040 | WL | WSLII-800D/72.5-6x5A |  |  | skip | no transformer I |  | 72.5 |  |  | D | II
E-W260041-042 | WL | WSLVIII-800D/72.5-5x2B | WSLII-1000D/72.5-6x5A | WSLII-1200D/72.5-6x5A | family |  | 794 | 72.5 | 0 |  | D | III
E-W260043-044 | WL | WSLIV-600Y/72.5-6x5A | WSLIV-600Y/72.5-6x5A | WSLIV-800Y/72.5-6x5A | exact |  | 395 | 72.5 | 0 | 2 | Y | III
E-W260045 | WL | WSLIV-600D/126-6x5D | WSLII-600D/126-6x5B | WSLII-800D/126-6x5B | family |  | 289.4 | 126 | 0 | 2 | D | III
E-W260046 | WL | WSLIV-600Y/72.5-6x5A | WSLIV-600Y/72.5-6x5A | WSLIV-800Y/72.5-6x5A | exact |  | 395 | 72.5 | 0 | 2 | Y | III