- Power    = 10 MVA     ONAN 
Voltage = 33 / 11.5 kV

three phase
f = 50 Hz 
Connection Group = Dyn11 
Tapping steps and range = + / - 8  x 1.25 %  , Coarse - Fine   
Tappings on HV side ( 33kV , Delta connected ) 
* Rated lightning impulse withstand voltage for HV : 170 kV peak 
*AC withstand voltage for HV : 70kV r.m.s. 
Ambient Temperature : -40 / + 50 degree Celsius

Insulation Across tap winding:  AC: 30kv  BIL 120KV

Max. Rated through current: 112.24A

Step voltage: 412.5V

Rated step capacity: 46.3kVA

Selected model: CV2III-350D/40.5-10193G

- 103 MVA Power Transformer, 138KV/33KV, three phase

138 kV ± 8 x 1.5 % (plus/minus regulation)

Reversing regulation

Star connection, regulation at neutral point

Insulation to ground: AC: 140KV； BIL 350KV

Insulation Across tap winding:  AC: 65kv  BIL 285KV

Max. Rated through current: 489.7A

Step voltage: 1195.2V

Rated step capacity: 585.26kVA

Selected model: CM2III-600Y/72.5C-10193W

- Autotransformer:  250MVA/230KV/115KV, three phase

230 kV ± 8 x 1.25 % (COARSE FINE regulation)

Star connected, regulated at the middle of the winding

Tap changer Insulation to ground: AC: 325KV； BIL 750KV

Insulation Across tap winding:  AC: 100kv  BIL 450KV

Max. Rated through current: 697.3A

Step voltage: 1659.9V

Rated step capacity: 1157.48

Selected model: 3xSHZVI-1000/170D-10193G

- Furnace transformer: 15MVA/35KV/380V, single phase

30 Positions, linear regulation,

Regulation at end of the winding, star connected

Max. Rated through current:

Step voltage:

Rated step capacity:

Selected model: CMI-800/72.5B-32300

- 120MVA/132KV/11KV, 3PH

132 kV ± 10 x 1.25 %, regulation at the middle of delta connected winding.

Tap changer Insulation to ground: BIL 650KV AC 275KV

Insulation Across tap winding:  AC: 50kv BIL 200KV

Max. Rated through current: 346.34A

Step voltage: 1650V

Rated step capacity: 571.46kVA

Selected model: CV2III-600D/145-12233W

- 333MVA/500KV/220KV single phase

500 kV ± 13 x 1.25 %, regulation on the neutral point

Tap changer Insulation to ground: BIL 1050KV AC 460 KV

Insulation Across tap winding:  AC: 110kv BIL 520KV

Max. Rated through current: 1377.33A

Step voltage: 3608.5V

Rated step capacity: 4970.15kVA

Selected model: SHZVGI-2000/252DE-14271W

- 220MVA/132/11KV three phase

132 kV ± 9 x 1.25 %,

Regulation at the end of the winding, delta connected.

Insulation Across tap winding:  AC: 80kv BIL 320KV

Max. Rated through current: 626.01A

Step voltage: 1650V

Rated step capacity: 1032.92kV

Selected model: 3xCM2I-800/72.5B-10191W